## Step1
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct | study_ratio_l_per_m2
short_term | Short / Mid-Term Storage | 50 | 10 | 580.8333 | 30 | 34.8731 | 35 | 1 | TRUE | 1 | 300 | 15000 | 8435.8342 | 1171.7917 | 144.0124 | 1315.8041 | 28283.3689 | 9085.0924 | 402.1453 | 161.9667 | 115.6905 | 9602.9282 | 9649.2044 | 4038.3956 | 1200.1035 | 46.2762 | 18578.1991 | 620.0773 | 517.8358 | 45.632 | 13687.6 | 70.496 | 29.504 | 200
short_term | Short / Mid-Term Storage | 100 | 20 | 1161.6667 | 30 | 52.1316 | 35 | 1 | TRUE | 1 | 300 | 30000 | 14485.4314 | 2224.2716 | 7.1632 | 2231.4348 | 55598.994 | 12858.5675 | 620.1049 | 0 | 0 | 13478.6724 | 13478.6724 | 208.9276 | 59.6936 | 0 | 41483.5439 | 1256.8826 | 620.1049 | 122.5868 | 13687.6 | 98.4736 | 1.5264 | 200

## Step2
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct
short_term | Short / Mid-Term Storage | 100 | 20 | 1161.6667 | 30 | 52.1316 | 35 | 1 | TRUE | 1 | 300 | 30000 | 14485.4314 | 2224.2716 | 7.1632 | 2231.4348 | 55598.994 | 12858.5675 | 620.1049 | 0 | 0 | 13478.6724 | 13478.6724 | 208.9276 | 59.6936 | 0 | 41483.5439 | 1256.8826 | 620.1049 | 122.5868 | 13687.6 | 98.4736 | 1.5264
short_term | Short / Mid-Term Storage | 100 | 50 | 2904.1667 | 30 | 65.9305 | 35 | 1 | TRUE | 1 | 300 | 30000 | 29602.2443 | 2980.1122 | 7.1632 | 2987.2754 | 55610.7632 | 12741.3475 | 737.3249 | 0 | 0 | 13478.6724 | 13478.6724 | 208.9276 | 59.6936 | 0 | 39739.1123 | 3130.3033 | 737.3249 | 306.0166 | 13687.6 | 98.4736 | 1.5264

## FinalHourly
timestamp | simulation_year_index | tank_type | tank_type_label | outside_temp_c | solar_rad_kwh_m2 | horizontal_solar_rad_kwh_m2 | heating_load_kwh | collector_efficiency | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_heating_total_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | tank_temp_start_c | tank_temp_end_c | tank_top_temp_start_c | tank_bottom_temp_start_c | tank_top_temp_end_c | tank_bottom_temp_end_c | tank_stored_energy_kwh | tank_charge_kwh | tank_discharge_direct_kwh | tank_discharge_hp_source_kwh | tank_discharge_total_kwh | tank_loss_kwh | solar_energy_curtailed_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated
2025-01-01 | 1 | short_term | Short / Mid-Term Storage | -10 | 1 |  | 60 | 0.528 | 52.8 | 52.8 | 0 | 0 | 0 | 52.8 | 7.2 | 2.0571 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2469 | 8.1647 | 8.4115
2025-01-01 01:00 | 1 | short_term | Short / Mid-Term Storage | -10 | 1 |  | 60 | 0.528 | 52.8 | 52.8 | 0 | 0 | 0 | 52.8 | 7.2 | 2.0571 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2469 | 8.1647 | 8.4115
2025-01-01 02:00 | 1 | short_term | Short / Mid-Term Storage | -9.99 | 1 |  | 59.99 | 0.528 | 52.8032 | 52.8032 | 0 | 0 | 0 | 52.8032 | 7.1868 | 2.0534 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2464 | 8.1647 | 8.4111
2025-01-01 03:00 | 1 | short_term | Short / Mid-Term Storage | -9.98 | 1 |  | 59.97 | 0.5281 | 52.8064 | 52.8064 | 0 | 0 | 0 | 52.8064 | 7.1636 | 2.0467 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2456 | 8.1647 | 8.4103
2025-01-01 04:00 | 1 | short_term | Short / Mid-Term Storage | -9.96 | 1 |  | 59.95 | 0.5281 | 52.8128 | 52.8128 | 0 | 0 | 0 | 52.8128 | 7.1372 | 2.0392 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2447 | 8.1647 | 8.4094
2025-01-01 05:00 | 1 | short_term | Short / Mid-Term Storage | -9.94 | 1 |  | 59.92 | 0.5282 | 52.8192 | 52.8192 | 0 | 0 | 0 | 52.8192 | 7.1008 | 2.0288 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2435 | 8.1647 | 8.4081
2025-01-01 06:00 | 1 | short_term | Short / Mid-Term Storage | -9.92 | 1 |  | 59.88 | 0.5283 | 52.8256 | 52.8256 | 0 | 0 | 0 | 52.8256 | 7.0544 | 2.0155 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2419 | 8.1647 | 8.4066
2025-01-01 07:00 | 1 | short_term | Short / Mid-Term Storage | -9.89 | 1 |  | 59.84 | 0.5284 | 52.8352 | 52.8352 | 0 | 0 | 0 | 52.8352 | 7.0048 | 2.0014 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2402 | 8.1647 | 8.4049
2025-01-01 08:00 | 1 | short_term | Short / Mid-Term Storage | -9.86 | 1 |  | 59.79 | 0.5284 | 52.8448 | 52.8448 | 0 | 0 | 0 | 52.8448 | 6.9452 | 1.9843 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2381 | 8.1647 | 8.4028
2025-01-01 09:00 | 1 | short_term | Short / Mid-Term Storage | -9.82 | 1 |  | 59.73 | 0.5286 | 52.8576 | 52.8576 | 0 | 0 | 0 | 52.8576 | 6.8724 | 1.9635 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2356 | 8.1647 | 8.4003
2025-01-01 10:00 | 1 | short_term | Short / Mid-Term Storage | -9.78 | 1 |  | 59.67 | 0.5287 | 52.8704 | 52.8704 | 0 | 0 | 0 | 52.8704 | 6.7996 | 1.9427 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2331 | 8.1647 | 8.3978
2025-01-01 11:00 | 1 | short_term | Short / Mid-Term Storage | -9.73 | 1 |  | 59.6 | 0.5289 | 52.8864 | 52.8864 | 0 | 0 | 0 | 52.8864 | 6.7136 | 1.9182 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2302 | 8.1647 | 8.3949
2025-01-01 12:00 | 1 | short_term | Short / Mid-Term Storage | -9.68 | 1 |  | 59.52 | 0.529 | 52.9024 | 52.9024 | 0 | 0 | 0 | 52.9024 | 6.6176 | 1.8907 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2269 | 8.1647 | 8.3916
2025-01-01 13:00 | 1 | short_term | Short / Mid-Term Storage | -9.63 | 1 |  | 59.44 | 0.5292 | 52.9184 | 52.9184 | 0 | 0 | 0 | 52.9184 | 6.5216 | 1.8633 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2236 | 8.1647 | 8.3883
2025-01-01 14:00 | 1 | short_term | Short / Mid-Term Storage | -9.57 | 1 |  | 59.35 | 0.5294 | 52.9376 | 52.9376 | 0 | 0 | 0 | 52.9376 | 6.4124 | 1.8321 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2199 | 8.1647 | 8.3845
2025-01-01 15:00 | 1 | short_term | Short / Mid-Term Storage | -9.5 | 1 |  | 59.25 | 0.5296 | 52.96 | 52.96 | 0 | 0 | 0 | 52.96 | 6.29 | 1.7971 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2157 | 8.1647 | 8.3803
2025-01-01 16:00 | 1 | short_term | Short / Mid-Term Storage | -9.43 | 1 |  | 59.15 | 0.5298 | 52.9824 | 52.9824 | 0 | 0 | 0 | 52.9824 | 6.1676 | 1.7622 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2115 | 8.1647 | 8.3762
2025-01-01 17:00 | 1 | short_term | Short / Mid-Term Storage | -9.36 | 1 |  | 59.04 | 0.53 | 53.0048 | 53.0048 | 0 | 0 | 0 | 53.0048 | 6.0352 | 1.7243 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2069 | 8.1647 | 8.3716
2025-01-01 18:00 | 1 | short_term | Short / Mid-Term Storage | -9.29 | 1 |  | 58.93 | 0.5303 | 53.0272 | 53.0272 | 0 | 0 | 0 | 53.0272 | 5.9028 | 1.6865 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2024 | 8.1647 | 8.3671
2025-01-01 19:00 | 1 | short_term | Short / Mid-Term Storage | -9.2 | 1 |  | 58.81 | 0.5306 | 53.056 | 53.056 | 0 | 0 | 0 | 53.056 | 5.754 | 1.644 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1973 | 8.1647 | 8.362
2025-01-01 20:00 | 1 | short_term | Short / Mid-Term Storage | -9.12 | 1 |  | 58.68 | 0.5308 | 53.0816 | 53.0816 | 0 | 0 | 0 | 53.0816 | 5.5984 | 1.5995 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1919 | 8.1647 | 8.3566
2025-01-01 21:00 | 1 | short_term | Short / Mid-Term Storage | -9.03 | 1 |  | 58.55 | 0.5311 | 53.1104 | 53.1104 | 0 | 0 | 0 | 53.1104 | 5.4396 | 1.5542 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1865 | 8.1647 | 8.3512
2025-01-01 22:00 | 1 | short_term | Short / Mid-Term Storage | -8.94 | 1 |  | 58.41 | 0.5314 | 53.1392 | 53.1392 | 0 | 0 | 0 | 53.1392 | 5.2708 | 1.5059 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1807 | 8.1647 | 8.3454
2025-01-01 23:00 | 1 | short_term | Short / Mid-Term Storage | -8.84 | 1 |  | 58.26 | 0.5317 | 53.1712 | 53.1712 | 0 | 0 | 0 | 53.1712 | 5.0888 | 1.4539 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1745 | 8.1647 | 8.3392
2025-01-02 | 1 | short_term | Short / Mid-Term Storage | -8.74 | 1 |  | 58.11 | 0.532 | 53.2032 | 53.2032 | 0 | 0 | 0 | 53.2032 | 4.9068 | 1.4019 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1682 | 8.1647 | 8.3329
2025-01-02 01:00 | 1 | short_term | Short / Mid-Term Storage | -8.63 | 1 |  | 57.95 | 0.5324 | 53.2384 | 53.2384 | 0 | 0 | 0 | 53.2384 | 4.7116 | 1.3462 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1615 | 8.1647 | 8.3262
2025-01-02 02:00 | 1 | short_term | Short / Mid-Term Storage | -8.52 | 1 |  | 57.78 | 0.5327 | 53.2736 | 53.2736 | 0 | 0 | 0 | 53.2736 | 4.5064 | 1.2875 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1545 | 8.1647 | 8.3192
2025-01-02 03:00 | 1 | short_term | Short / Mid-Term Storage | -8.41 | 1 |  | 57.61 | 0.5331 | 53.3088 | 53.3088 | 0 | 0 | 0 | 53.3088 | 4.3012 | 1.2289 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1475 | 8.1647 | 8.3122
2025-01-02 04:00 | 1 | short_term | Short / Mid-Term Storage | -8.29 | 1 |  | 57.44 | 0.5335 | 53.3472 | 53.3472 | 0 | 0 | 0 | 53.3472 | 4.0928 | 1.1694 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1403 | 8.1647 | 8.305
2025-01-02 05:00 | 1 | short_term | Short / Mid-Term Storage | -8.17 | 1 |  | 57.25 | 0.5339 | 53.3856 | 53.3856 | 0 | 0 | 0 | 53.3856 | 3.8644 | 1.1041 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1325 | 8.1647 | 8.2972
2025-01-02 06:00 | 1 | short_term | Short / Mid-Term Storage | -8.04 | 1 |  | 57.07 | 0.5343 | 53.4272 | 53.4272 | 0 | 0 | 0 | 53.4272 | 3.6428 | 1.0408 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1249 | 8.1647 | 8.2896
2025-01-02 07:00 | 1 | short_term | Short / Mid-Term Storage | -7.91 | 1 |  | 56.87 | 0.5347 | 53.4688 | 53.4688 | 0 | 0 | 0 | 53.4688 | 3.4012 | 0.9718 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1166 | 8.1647 | 8.2813
2025-01-02 08:00 | 1 | short_term | Short / Mid-Term Storage | -7.78 | 1 |  | 56.67 | 0.5351 | 53.5104 | 53.5104 | 0 | 0 | 0 | 53.5104 | 3.1596 | 0.9027 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1083 | 8.1647 | 8.273
2025-01-02 09:00 | 1 | short_term | Short / Mid-Term Storage | -7.64 | 1 |  | 56.47 | 0.5356 | 53.5552 | 53.5552 | 0 | 0 | 0 | 53.5552 | 2.9148 | 0.8328 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 8.1647 | 8.2646
2025-01-02 10:00 | 1 | short_term | Short / Mid-Term Storage | -7.5 | 1 |  | 56.26 | 0.536 | 53.6 | 53.6 | 0 | 0 | 0 | 53.6 | 2.66 | 0.76 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0912 | 8.1647 | 8.2559
2025-01-02 11:00 | 1 | short_term | Short / Mid-Term Storage | -7.36 | 1 |  | 56.04 | 0.5364 | 53.6448 | 53.6448 | 0 | 0 | 0 | 53.6448 | 2.3952 | 0.6843 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0821 | 8.1647 | 8.2468
2025-01-02 12:00 | 1 | short_term | Short / Mid-Term Storage | -7.21 | 1 |  | 55.82 | 0.5369 | 53.6928 | 53.6928 | 0 | 0 | 0 | 53.6928 | 2.1272 | 0.6078 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0729 | 8.1647 | 8.2376
2025-01-02 13:00 | 1 | short_term | Short / Mid-Term Storage | -7.06 | 1 |  | 55.59 | 0.5374 | 53.7408 | 53.7408 | 0 | 0 | 0 | 53.7408 | 1.8492 | 0.5283 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0634 | 8.1647 | 8.2281
2025-01-02 14:00 | 1 | short_term | Short / Mid-Term Storage | -6.9 | 1 |  | 55.36 | 0.5379 | 53.792 | 53.792 | 0 | 0 | 0 | 53.792 | 1.568 | 0.448 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0538 | 8.1647 | 8.2185
2025-01-02 15:00 | 1 | short_term | Short / Mid-Term Storage | -6.74 | 1 |  | 55.12 | 0.5384 | 53.8432 | 53.8432 | 0 | 0 | 0 | 53.8432 | 1.2768 | 0.3648 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0438 | 8.1647 | 8.2085
2025-01-02 16:00 | 1 | short_term | Short / Mid-Term Storage | -6.58 | 1 |  | 54.87 | 0.5389 | 53.8944 | 53.8944 | 0 | 0 | 0 | 53.8944 | 0.9756 | 0.2787 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0334 | 8.1647 | 8.1981
2025-01-02 17:00 | 1 | short_term | Short / Mid-Term Storage | -6.42 | 1 |  | 54.62 | 0.5395 | 53.9456 | 53.9456 | 0 | 0 | 0 | 53.9456 | 0.6744 | 0.1927 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0231 | 8.1647 | 8.1878
2025-01-02 18:00 | 1 | short_term | Short / Mid-Term Storage | -6.25 | 1 |  | 54.37 | 0.54 | 54 | 54 | 0 | 0 | 0 | 54 | 0.37 | 0.1057 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0127 | 8.1647 | 8.1774
2025-01-02 19:00 | 1 | short_term | Short / Mid-Term Storage | -6.07 | 1 |  | 54.11 | 0.5406 | 54.0576 | 54.0576 | 0 | 0 | 0 | 54.0576 | 0.0524 | 0.015 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018 | 8.1647 | 8.1665
2025-01-02 20:00 | 1 | short_term | Short / Mid-Term Storage | -5.9 | 1 |  | 53.85 | 0.5411 | 54.112 | 53.85 | 0 | 0 | 0 | 53.85 | 0 | 0 | 0 | 30 | 30.0045 | 30 | 30 | 30.0361 | 30 | 0.2619 | 0.262 | 0 | 0 | 0 | 0.0001 | 0 | 0 | 8.1647 | 8.1647
2025-01-02 21:00 | 1 | short_term | Short / Mid-Term Storage | -5.72 | 1 |  | 53.58 | 0.5417 | 54.1696 | 53.58 | 0 | 0 | 0 | 53.58 | 0 | 0 | 0 | 30.0045 | 30.0147 | 30.0361 | 30 | 30.1172 | 30 | 0.8511 | 0.5896 | 0 | 0 | 0 | 0.0004 | 0 | 0 | 8.1647 | 8.1647
2025-01-02 22:00 | 1 | short_term | Short / Mid-Term Storage | -5.54 | 1 |  | 53.31 | 0.5423 | 54.2272 | 53.31 | 0 | 0 | 0 | 53.31 | 0 | 0 | 0 | 30.0147 | 30.0304 | 30.1172 | 30 | 30.2435 | 30 | 1.7676 | 0.9172 | 0 | 0 | 0 | 0.0007 | 0 | 0 | 8.1647 | 8.1647
2025-01-02 23:00 | 1 | short_term | Short / Mid-Term Storage | -5.35 | 1 |  | 53.03 | 0.5429 | 54.288 | 53.03 | 0 | 0 | 0 | 53.03 | 0 | 0 | 0 | 30.0304 | 30.0521 | 30.2435 | 30 | 30.4166 | 30 | 3.0243 | 1.258 | 0 | 0 | 0 | 0.0013 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 | 1 | short_term | Short / Mid-Term Storage | -5.16 | 1 |  | 52.75 | 0.5435 | 54.3488 | 52.75 | 0 | 0 | 0 | 52.75 | 0 | 0 | 0 | 30.0521 | 30.0796 | 30.4166 | 30 | 30.6365 | 30 | 4.6212 | 1.5988 | 0 | 0 | 0 | 0.0019 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 01:00 | 1 | short_term | Short / Mid-Term Storage | -4.97 | 1 |  | 52.46 | 0.5441 | 54.4096 | 52.46 | 0 | 0 | 0 | 52.46 | 0 | 0 | 0 | 30.0796 | 30.1131 | 30.6365 | 30 | 30.9046 | 30 | 6.568 | 1.9496 | 0 | 0 | 0 | 0.0028 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 02:00 | 1 | short_term | Short / Mid-Term Storage | -4.78 | 1 |  | 52.17 | 0.5447 | 54.4704 | 52.17 | 0 | 0 | 0 | 52.17 | 0 | 0 | 0 | 30.1131 | 30.1526 | 30.9046 | 30 | 31.221 | 30 | 8.8647 | 2.3004 | 0 | 0 | 0 | 0.0037 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 03:00 | 1 | short_term | Short / Mid-Term Storage | -4.58 | 1 |  | 51.87 | 0.5453 | 54.5344 | 51.87 | 0 | 0 | 0 | 51.87 | 0 | 0 | 0 | 30.1526 | 30.1984 | 31.221 | 30 | 31.5873 | 30 | 11.5243 | 2.6644 | 0 | 0 | 0 | 0.0048 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 04:00 | 1 | short_term | Short / Mid-Term Storage | -4.38 | 1 |  | 51.57 | 0.546 | 54.5984 | 51.57 | 0 | 0 | 0 | 51.57 | 0 | 0 | 0 | 30.1984 | 30.2504 | 31.5873 | 30 | 32.0035 | 30 | 14.5466 | 3.0284 | 0 | 0 | 0 | 0.0061 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 05:00 | 1 | short_term | Short / Mid-Term Storage | -4.18 | 1 |  | 51.27 | 0.5466 | 54.6624 | 51.27 | 0 | 0 | 0 | 51.27 | 0 | 0 | 0 | 30.2504 | 30.3087 | 32.0035 | 30 | 32.4698 | 30 | 17.9315 | 3.3924 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 06:00 | 1 | short_term | Short / Mid-Term Storage | -3.97 | 1 |  | 50.96 | 0.5473 | 54.7296 | 50.96 | 0 | 0 | 0 | 50.96 | 0 | 0 | 0 | 30.3087 | 30.3735 | 32.4698 | 30 | 32.9877 | 30 | 21.692 | 3.7696 | 0 | 0 | 0 | 0.0091 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 07:00 | 1 | short_term | Short / Mid-Term Storage | -3.76 | 1 |  | 50.65 | 0.548 | 54.7968 | 50.65 | 0 | 0 | 0 | 50.65 | 0 | 0 | 0 | 30.3735 | 30.4447 | 32.9877 | 30 | 33.5574 | 30 | 25.828 | 4.1468 | 0 | 0 | 0 | 0.0108 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 08:00 | 1 | short_term | Short / Mid-Term Storage | -3.55 | 1 |  | 50.33 | 0.5486 | 54.864 | 50.33 | 0 | 0 | 0 | 50.33 | 0 | 0 | 0 | 30.4447 | 30.5225 | 33.5574 | 30 | 34.1801 | 30 | 30.3493 | 4.534 | 0 | 0 | 0 | 0.0127 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 09:00 | 1 | short_term | Short / Mid-Term Storage | -3.34 | 1 |  | 50.01 | 0.5493 | 54.9312 | 50.01 | 0 | 0 | 0 | 50.01 | 0 | 0 | 0 | 30.5225 | 30.607 | 34.1801 | 30 | 34.8559 | 30 | 35.2557 | 4.9212 | 0 | 0 | 0 | 0.0148 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 10:00 | 1 | short_term | Short / Mid-Term Storage | -3.12 | 1 |  | 49.69 | 0.55 | 55.0016 | 49.69 | 0 | 0 | 0 | 49.69 | 0 | 0 | 0 | 30.607 | 30.6981 | 34.8559 | 30 | 35.5851 | 30 | 40.5503 | 5.3116 | 0 | 0 | 0 | 0.017 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 11:00 | 1 | short_term | Short / Mid-Term Storage | -2.91 | 1 |  | 49.36 | 0.5507 | 55.0688 | 49.36 | 0 | 0 | 0 | 49.36 | 0 | 0 | 0 | 30.6981 | 30.7961 | 35.5851 | 30 | 36.3687 | 30 | 46.2398 | 5.7088 | 0 | 0 | 0 | 0.0194 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 12:00 | 1 | short_term | Short / Mid-Term Storage | -2.69 | 1 |  | 49.03 | 0.5514 | 55.1392 | 49.03 | 0 | 0 | 0 | 49.03 | 0 | 0 | 0 | 30.7961 | 30.9009 | 36.3687 | 30 | 37.2072 | 30 | 52.327 | 6.1092 | 0 | 0 | 0 | 0.0219 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 13:00 | 1 | short_term | Short / Mid-Term Storage | -2.46 | 1 |  | 48.69 | 0.5521 | 55.2128 | 48.69 | 0 | 0 | 0 | 48.69 | 0 | 0 | 0 | 30.9009 | 31.0128 | 37.2072 | 30 | 38.1022 | 30 | 58.8252 | 6.5228 | 0 | 0 | 0 | 0.0246 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 14:00 | 1 | short_term | Short / Mid-Term Storage | -2.24 | 1 |  | 48.36 | 0.5528 | 55.2832 | 48.36 | 0 | 0 | 0 | 48.36 | 0 | 0 | 0 | 31.0128 | 31.1315 | 38.1022 | 30 | 39.0519 | 30 | 65.7209 | 6.9232 | 0 | 0 | 0 | 0.0275 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 15:00 | 1 | short_term | Short / Mid-Term Storage | -2.01 | 1 |  | 48.02 | 0.5536 | 55.3568 | 48.02 | 0 | 0 | 0 | 48.02 | 0 | 0 | 0 | 31.1315 | 31.2573 | 39.0519 | 30 | 40.0583 | 30 | 73.0271 | 7.3368 | 0 | 0 | 0 | 0.0306 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 16:00 | 1 | short_term | Short / Mid-Term Storage | -1.78 | 1 |  | 47.67 | 0.5543 | 55.4304 | 47.67 | 0 | 0 | 0 | 47.67 | 0 | 0 | 0 | 31.2573 | 31.3903 | 40.0583 | 30 | 41.1225 | 30 | 80.7537 | 7.7604 | 0 | 0 | 0 | 0.0338 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 17:00 | 1 | short_term | Short / Mid-Term Storage | -1.55 | 1 |  | 47.32 | 0.555 | 55.504 | 47.32 | 0 | 0 | 0 | 47.32 | 0 | 0 | 0 | 31.3903 | 31.5306 | 41.1225 | 30 | 42.2445 | 30 | 88.9004 | 8.184 | 0 | 0 | 0 | 0.0372 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 18:00 | 1 | short_term | Short / Mid-Term Storage | -1.32 | 1 |  | 46.97 | 0.5558 | 55.5776 | 46.97 | 0 | 0 | 0 | 46.97 | 0 | 0 | 0 | 31.5306 | 31.6781 | 42.2445 | 30 | 43.4245 | 30 | 97.4672 | 8.6076 | 0 | 0 | 0 | 0.0408 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 19:00 | 1 | short_term | Short / Mid-Term Storage | -1.08 | 1 |  | 46.62 | 0.5565 | 55.6544 | 46.62 | 0 | 0 | 0 | 46.62 | 0 | 0 | 0 | 31.6781 | 31.8328 | 43.4245 | 30 | 44.6627 | 30 | 106.457 | 9.0344 | 0 | 0 | 0 | 0.0446 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 20:00 | 1 | short_term | Short / Mid-Term Storage | -0.84 | 1 |  | 46.27 | 0.5573 | 55.7312 | 46.27 | 0 | 0 | 0 | 46.27 | 0 | 0 | 0 | 31.8328 | 31.9949 | 44.6627 | 30 | 45.9591 | 30 | 115.8697 | 9.4612 | 0 | 0 | 0 | 0.0485 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 21:00 | 1 | short_term | Short / Mid-Term Storage | -0.61 | 1 |  | 45.91 | 0.555 | 55.4979 | 45.91 | 0 | 0 | 0 | 45.91 | 0 | 0 | 0 | 31.9949 | 32.1591 | 45.9591 | 30 | 47.2724 | 30 | 125.405 | 9.5879 | 0 | 0 | 0 | 0.0525 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 22:00 | 1 | short_term | Short / Mid-Term Storage | -0.37 | 1 |  | 45.55 | 0.5515 | 55.1544 | 45.55 | 0 | 0 | 0 | 45.55 | 0 | 0 | 0 | 32.1591 | 32.3234 | 47.2724 | 30 | 48.5875 | 30 | 134.9529 | 9.6044 | 0 | 0 | 0 | 0.0565 | 0 | 0 | 8.1647 | 8.1647
2025-01-03 23:00 | 1 | short_term | Short / Mid-Term Storage | -0.12 | 1 |  | 45.19 | 0.5481 | 54.8136 | 45.19 | 0 | 0 | 0 | 45.19 | 0 | 0 | 0 | 32.3234 | 32.4881 | 48.5875 | 30 | 49.9046 | 30 | 144.516 | 9.6236 | 0 | 0 | 0 | 0.0605 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 | 1 | short_term | Short / Mid-Term Storage | 0.12 | 1 |  | 44.82 | 0.5447 | 54.4689 | 44.82 | 0 | 0 | 0 | 44.82 | 0 | 0 | 0 | 32.4881 | 32.6531 | 49.9046 | 30 | 51.2247 | 30 | 154.1004 | 9.6489 | 0 | 0 | 0 | 0.0645 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 01:00 | 1 | short_term | Short / Mid-Term Storage | 0.36 | 1 |  | 44.45 | 0.5412 | 54.1233 | 44.45 | 0 | 0 | 0 | 44.45 | 0 | 0 | 0 | 32.6531 | 32.8185 | 51.2247 | 30 | 52.5476 | 30 | 163.7051 | 9.6733 | 0 | 0 | 0 | 0.0686 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 02:00 | 1 | short_term | Short / Mid-Term Storage | 0.61 | 1 |  | 44.08 | 0.5378 | 53.78 | 44.08 | 0 | 0 | 0 | 44.08 | 0 | 0 | 0 | 32.8185 | 32.9842 | 52.5476 | 30 | 53.8736 | 30 | 173.3325 | 9.7 | 0 | 0 | 0 | 0.0726 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 03:00 | 1 | short_term | Short / Mid-Term Storage | 0.86 | 1 |  | 43.71 | 0.5344 | 53.4356 | 43.71 | 0 | 0 | 0 | 43.71 | 0 | 0 | 0 | 32.9842 | 33.1503 | 53.8736 | 30 | 55.2026 | 30 | 182.9815 | 9.7256 | 0 | 0 | 0 | 0.0766 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 04:00 | 1 | short_term | Short / Mid-Term Storage | 1.11 | 1 |  | 43.34 | 0.5309 | 53.0904 | 43.34 | 0 | 0 | 0 | 43.34 | 0 | 0 | 0 | 33.1503 | 33.3168 | 55.2026 | 30 | 56.5344 | 30 | 192.6511 | 9.7504 | 0 | 0 | 0 | 0.0807 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 05:00 | 1 | short_term | Short / Mid-Term Storage | 1.36 | 1 |  | 42.96 | 0.5274 | 52.7442 | 42.96 | 0 | 0 | 0 | 42.96 | 0 | 0 | 0 | 33.3168 | 33.4838 | 56.5344 | 30 | 57.8704 | 30 | 202.3506 | 9.7842 | 0 | 0 | 0 | 0.0848 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 06:00 | 1 | short_term | Short / Mid-Term Storage | 1.61 | 1 |  | 42.59 | 0.524 | 52.3967 | 42.59 | 0 | 0 | 0 | 42.59 | 0 | 0 | 0 | 33.4838 | 33.6511 | 57.8704 | 30 | 59.2088 | 30 | 212.0684 | 9.8067 | 0 | 0 | 0 | 0.0888 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 07:00 | 1 | short_term | Short / Mid-Term Storage | 1.86 | 1 |  | 42.21 | 0.5205 | 52.0484 | 42.21 | 0 | 0 | 0 | 42.21 | 0 | 0 | 0 | 33.6511 | 33.8189 | 59.2088 | 30 | 60.5511 | 30 | 221.8139 | 9.8384 | 0 | 0 | 0 | 0.0929 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 08:00 | 1 | short_term | Short / Mid-Term Storage | 2.11 | 1 |  | 41.83 | 0.517 | 51.6988 | 41.83 | 0 | 0 | 0 | 41.83 | 0 | 0 | 0 | 33.8189 | 33.9871 | 60.5511 | 30 | 61.897 | 30 | 231.5857 | 9.8688 | 0 | 0 | 0 | 0.097 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 09:00 | 1 | short_term | Short / Mid-Term Storage | 2.37 | 1 |  | 41.45 | 0.5135 | 51.3514 | 41.45 | 0 | 0 | 0 | 41.45 | 0 | 0 | 0 | 33.9871 | 34.1559 | 61.897 | 30 | 63.2468 | 30 | 241.386 | 9.9014 | 0 | 0 | 0 | 0.1011 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 10:00 | 1 | short_term | Short / Mid-Term Storage | 2.62 | 1 |  | 41.07 | 0.51 | 50.9994 | 41.07 | 0 | 0 | 0 | 41.07 | 0 | 0 | 0 | 34.1559 | 34.325 | 63.2468 | 30 | 64.6 | 30 | 251.2101 | 9.9294 | 0 | 0 | 0 | 0.1052 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 11:00 | 1 | short_term | Short / Mid-Term Storage | 2.88 | 1 |  | 40.68 | 0.5065 | 50.6496 | 40.68 | 0 | 0 | 0 | 40.68 | 0 | 0 | 0 | 34.325 | 34.4948 | 64.6 | 30 | 65.958 | 30 | 261.0704 | 9.9696 | 0 | 0 | 0 | 0.1093 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 12:00 | 1 | short_term | Short / Mid-Term Storage | 3.13 | 1 |  | 40.3 | 0.503 | 50.295 | 40.3 | 0 | 0 | 0 | 40.3 | 0 | 0 | 0 | 34.4948 | 34.6649 | 65.958 | 30 | 67.3191 | 30 | 270.9519 | 9.995 | 0 | 0 | 0 | 0.1135 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 13:00 | 1 | short_term | Short / Mid-Term Storage | 3.39 | 1 |  | 39.92 | 0.4994 | 49.9427 | 39.92 | 0 | 0 | 0 | 39.92 | 0 | 0 | 0 | 34.6649 | 34.8354 | 67.3191 | 30 | 68.6833 | 30 | 280.857 | 10.0227 | 0 | 0 | 0 | 0.1176 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 14:00 | 1 | short_term | Short / Mid-Term Storage | 3.65 | 1 |  | 39.53 | 0.4959 | 49.5893 | 39.53 | 0 | 0 | 0 | 39.53 | 0 | 0 | 0 | 34.8354 | 35.0065 | 68.6833 | 30 | 70.052 | 30 | 290.7945 | 10.0593 | 0 | 0 | 0 | 0.1218 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 15:00 | 1 | short_term | Short / Mid-Term Storage | 3.9 | 1 |  | 39.14 | 0.4923 | 49.2313 | 39.14 | 0 | 0 | 0 | 39.14 | 0 | 0 | 0 | 35.0065 | 35.1781 | 70.052 | 30 | 71.4246 | 30 | 300.7599 | 10.0913 | 0 | 0 | 0 | 0.126 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 16:00 | 1 | short_term | Short / Mid-Term Storage | 4.16 | 1 |  | 38.76 | 0.4888 | 48.8753 | 38.76 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 35.1781 | 35.35 | 71.4246 | 30 | 72.7999 | 30 | 310.7451 | 10.1153 | 0 | 0 | 0 | 0.1302 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 17:00 | 1 | short_term | Short / Mid-Term Storage | 4.42 | 1 |  | 38.37 | 0.4852 | 48.5184 | 38.37 | 0 | 0 | 0 | 38.37 | 0 | 0 | 0 | 35.35 | 35.5224 | 72.7999 | 30 | 74.1792 | 30 | 320.7592 | 10.1484 | 0 | 0 | 0 | 0.1344 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 18:00 | 1 | short_term | Short / Mid-Term Storage | 4.68 | 1 |  | 37.98 | 0.4816 | 48.1603 | 37.98 | 0 | 0 | 0 | 37.98 | 0 | 0 | 0 | 35.5224 | 35.6953 | 74.1792 | 30 | 75.5622 | 30 | 330.8009 | 10.1803 | 0 | 0 | 0 | 0.1386 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 19:00 | 1 | short_term | Short / Mid-Term Storage | 4.94 | 1 |  | 37.6 | 0.478 | 47.8009 | 37.6 | 0 | 0 | 0 | 37.6 | 0 | 0 | 0 | 35.6953 | 35.8684 | 75.5622 | 30 | 76.9476 | 30 | 340.859 | 10.2009 | 0 | 0 | 0 | 0.1428 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 20:00 | 1 | short_term | Short / Mid-Term Storage | 5.19 | 1.058 |  | 37.21 | 0.4878 | 51.6136 | 37.21 | 0 | 0 | 0 | 37.21 | 0 | 0 | 0 | 35.8684 | 36.1139 | 76.9476 | 30 | 78.9109 | 30 | 355.1138 | 14.4036 | 0 | 0 | 0 | 0.1487 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 21:00 | 1 | short_term | Short / Mid-Term Storage | 5.45 | 1.136 |  | 36.82 | 0.499 | 56.6845 | 36.82 | 0 | 0 | 0 | 36.82 | 0 | 0 | 0 | 36.1139 | 36.4532 | 78.9109 | 30 | 79.9791 | 30 | 374.8213 | 19.8645 | 0 | 0 | 0 | 0.157 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 22:00 | 1 | short_term | Short / Mid-Term Storage | 5.71 | 1.213 |  | 36.44 | 0.5109 | 61.9699 | 36.44 | 0 | 0 | 0 | 36.44 | 0 | 0 | 0 | 36.4532 | 36.8898 | 79.9791 | 30 | 79.9791 | 30 | 400.1836 | 25.5299 | 0 | 0 | 0 | 0.1676 | 0 | 0 | 8.1647 | 8.1647
2025-01-04 23:00 | 1 | short_term | Short / Mid-Term Storage | 5.97 | 1.29 |  | 36.05 | 0.524 | 67.5971 | 36.05 | 0 | 0 | 0 | 36.05 | 0 | 0 | 0 | 36.8898 | 37.4298 | 79.9791 | 30 | 79.9791 | 30 | 431.55 | 31.5471 | 0 | 0 | 0 | 0.1808 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 | 1 | short_term | Short / Mid-Term Storage | 6.23 | 1.368 |  | 35.66 | 0.5358 | 73.2963 | 35.66 | 0 | 0 | 0 | 35.66 | 0 | 0 | 0 | 37.4298 | 38.0744 | 79.9791 | 30 | 79.9791 | 30 | 468.9898 | 37.6363 | 0 | 0 | 0 | 0.1964 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 01:00 | 1 | short_term | Short / Mid-Term Storage | 6.48 | 1.445 |  | 35.28 | 0.5462 | 78.9203 | 35.28 | 0 | 0 | 0 | 35.28 | 0 | 0 | 0 | 38.0744 | 38.8221 | 79.9791 | 30 | 79.9791 | 30 | 512.4155 | 43.6403 | 0 | 0 | 0 | 0.2146 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 02:00 | 1 | short_term | Short / Mid-Term Storage | 6.74 | 1.522 |  | 34.89 | 0.5555 | 84.5475 | 34.89 | 0 | 0 | 0 | 34.89 | 0 | 0 | 0 | 38.8221 | 39.673 | 79.9791 | 30 | 79.9791 | 30 | 561.8377 | 49.6575 | 0 | 0 | 0 | 0.2353 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 03:00 | 1 | short_term | Short / Mid-Term Storage | 7 | 1.599 |  | 34.51 | 0.5639 | 90.1747 | 34.51 | 0 | 0 | 0 | 34.51 | 0 | 0 | 0 | 39.673 | 40.6269 | 79.9791 | 30 | 79.9791 | 30 | 617.2438 | 55.6647 | 0 | 0 | 0 | 0.2585 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 04:00 | 1 | short_term | Short / Mid-Term Storage | 7.25 | 1.675 |  | 34.12 | 0.5715 | 95.7267 | 34.12 | 0 | 0 | 0 | 34.12 | 0 | 0 | 0 | 40.6269 | 41.6826 | 79.9791 | 30 | 79.9791 | 30 | 678.5663 | 61.6067 | 0 | 0 | 0 | 0.2842 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 05:00 | 1 | short_term | Short / Mid-Term Storage | 7.51 | 1.752 |  | 33.74 | 0.5785 | 101.3539 | 33.74 | 0 | 0 | 0 | 33.74 | 0 | 0 | 0 | 41.6826 | 42.8413 | 79.9791 | 30 | 79.9791 | 30 | 745.8678 | 67.6139 | 0 | 0 | 0 | 0.3124 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 06:00 | 1 | short_term | Short / Mid-Term Storage | 7.76 | 1.828 |  | 33.36 | 0.5848 | 106.9059 | 33.36 | 0 | 0 | 0 | 33.36 | 0 | 0 | 0 | 42.8413 | 44.1016 | 79.9791 | 30 | 79.9791 | 30 | 819.0706 | 73.5459 | 0 | 0 | 0 | 0.3431 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 07:00 | 1 | short_term | Short / Mid-Term Storage | 8.01 | 1.904 |  | 32.98 | 0.5906 | 112.4579 | 32.98 | 0 | 0 | 0 | 32.98 | 0 | 0 | 0 | 44.1016 | 45.4635 | 79.9791 | 30 | 79.9791 | 30 | 898.1723 | 79.4779 | 0 | 0 | 0 | 0.3762 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 08:00 | 1 | short_term | Short / Mid-Term Storage | 8.27 | 1.98 |  | 32.6 | 0.596 | 118.0131 | 32.6 | 0 | 0 | 0 | 32.6 | 0 | 0 | 0 | 45.4635 | 46.9269 | 79.9791 | 30 | 79.9791 | 30 | 983.1736 | 85.4131 | 0 | 0 | 0 | 0.4118 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 09:00 | 1 | short_term | Short / Mid-Term Storage | 8.52 | 2.055 |  | 32.22 | 0.6009 | 123.4931 | 32.22 | 0 | 0 | 0 | 32.22 | 0 | 0 | 0 | 46.9269 | 48.4906 | 79.9791 | 30 | 79.9791 | 30 | 1073.9969 | 91.2731 | 0 | 0 | 0 | 0.4498 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 10:00 | 1 | short_term | Short / Mid-Term Storage | 8.77 | 2.13 |  | 31.85 | 0.6055 | 128.9731 | 31.85 | 0 | 0 | 0 | 31.85 | 0 | 0 | 0 | 48.4906 | 50.1543 | 79.9791 | 30 | 79.9791 | 30 | 1170.6297 | 97.1231 | 0 | 0 | 0 | 0.4903 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 11:00 | 1 | short_term | Short / Mid-Term Storage | 9.02 | 2.205 |  | 31.47 | 0.6098 | 134.4531 | 31.47 | 0 | 0 | 0 | 31.47 | 0 | 0 | 0 | 50.1543 | 51.9182 | 79.9791 | 30 | 79.9791 | 30 | 1273.0795 | 102.9831 | 0 | 0 | 0 | 0.5332 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 12:00 | 1 | short_term | Short / Mid-Term Storage | 9.27 | 2.28 |  | 31.1 | 0.6137 | 139.9331 | 31.1 | 0 | 0 | 0 | 31.1 | 0 | 0 | 0 | 51.9182 | 53.7819 | 79.9791 | 30 | 79.9791 | 30 | 1381.334 | 108.8331 | 0 | 0 | 0 | 0.5786 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 13:00 | 1 | short_term | Short / Mid-Term Storage | 9.51 | 2.354 |  | 30.73 | 0.6174 | 145.3379 | 30.73 | 0 | 0 | 0 | 30.73 | 0 | 0 | 0 | 53.7819 | 55.7443 | 79.9791 | 30 | 79.9791 | 30 | 1495.3156 | 114.6079 | 0 | 0 | 0 | 0.6263 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 14:00 | 1 | short_term | Short / Mid-Term Storage | 9.76 | 2.427 |  | 30.36 | 0.6208 | 150.6739 | 30.36 | 0 | 0 | 0 | 30.36 | 0 | 0 | 0 | 55.7443 | 57.8041 | 79.9791 | 30 | 79.9791 | 30 | 1614.9531 | 120.3139 | 0 | 0 | 0 | 0.6764 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 15:00 | 1 | short_term | Short / Mid-Term Storage | 10 | 2.501 |  | 30 | 0.6241 | 156.0787 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 57.8041 | 59.9622 | 79.9791 | 30 | 79.9791 | 30 | 1740.3029 | 126.0787 | 0 | 0 | 0 | 0.7289 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 16:00 | 1 | short_term | Short / Mid-Term Storage | 10.24 | 2.573 |  | 29.63 | 0.627 | 161.3395 | 29.63 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 59.9622 | 62.2163 | 79.9791 | 30 | 79.9791 | 30 | 1871.2286 | 131.7095 | 0 | 0 | 0 | 0.7838 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 17:00 | 1 | short_term | Short / Mid-Term Storage | 10.49 | 2.646 |  | 29.27 | 0.6299 | 166.6755 | 29.27 | 0 | 0 | 0 | 29.27 | 0 | 0 | 0 | 62.2163 | 64.5675 | 79.9791 | 30 | 79.9791 | 30 | 2007.7931 | 137.4055 | 0 | 0 | 0 | 0.841 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 18:00 | 1 | short_term | Short / Mid-Term Storage | 10.73 | 2.718 |  | 28.91 | 0.6326 | 171.9363 | 28.91 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 64.5675 | 67.0144 | 79.9791 | 30 | 79.9791 | 30 | 2149.9189 | 143.0263 | 0 | 0 | 0 | 0.9005 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 19:00 | 1 | short_term | Short / Mid-Term Storage | 10.96 | 2.789 |  | 28.56 | 0.6351 | 177.1219 | 28.56 | 0 | 0 | 0 | 28.56 | 0 | 0 | 0 | 67.0144 | 69.5556 | 79.9791 | 30 | 79.9791 | 30 | 2297.5185 | 148.5619 | 0 | 0 | 0 | 0.9623 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 20:00 | 1 | short_term | Short / Mid-Term Storage | 11.2 | 2.86 |  | 28.2 | 0.6374 | 182.3107 | 28.2 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 69.5556 | 72.1912 | 79.9791 | 30 | 79.9791 | 30 | 2450.6028 | 154.1107 | 0 | 0 | 0 | 1.0264 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 21:00 | 1 | short_term | Short / Mid-Term Storage | 11.43 | 2.93 |  | 27.85 | 0.6397 | 187.4243 | 27.85 | 0 | 0 | 0 | 27.85 | 0 | 0 | 0 | 72.1912 | 74.9197 | 79.9791 | 30 | 79.9791 | 39.5039 | 2609.0843 | 159.5743 | 0 | 0 | 0 | 1.0928 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 22:00 | 1 | short_term | Short / Mid-Term Storage | 11.67 | 3 |  | 27.5 | 0.6418 | 192.5411 | 27.5 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 74.9197 | 77.7411 | 79.9791 | 39.5039 | 79.9791 | 62.0756 | 2772.9639 | 165.0411 | 0 | 0 | 0 | 1.1615 | 0 | 0 | 8.1647 | 8.1647
2025-01-05 23:00 | 1 | short_term | Short / Mid-Term Storage | 11.9 | 3.069 |  | 27.16 | 0.6438 | 197.5827 | 27.16 | 0 | 0 | 0 | 27.16 | 0 | 0 | 0 | 77.7411 | 79.9791 | 79.9791 | 62.0756 | 79.9791 | 79.9791 | 2902.9508 | 131.2028 | 0 | 0 | 0 | 1.2159 | 39.2199 | 0 | 8.1647 | 8.1647
2025-01-06 | 1 | short_term | Short / Mid-Term Storage | 12.12 | 3.137 |  | 26.81 | 0.6457 | 202.5491 | 26.81 | 0 | 0 | 0 | 26.81 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 174.5232 | 0 | 8.1647 | 8.1647
2025-01-06 01:00 | 1 | short_term | Short / Mid-Term Storage | 12.35 | 3.205 |  | 26.47 | 0.6475 | 207.5187 | 26.47 | 0 | 0 | 0 | 26.47 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 179.8328 | 0 | 8.1647 | 8.1647
2025-01-06 02:00 | 1 | short_term | Short / Mid-Term Storage | 12.57 | 3.272 |  | 26.14 | 0.6492 | 212.4131 | 26.14 | 0 | 0 | 0 | 26.14 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 185.0572 | 0 | 8.1647 | 8.1647
2025-01-06 03:00 | 1 | short_term | Short / Mid-Term Storage | 12.8 | 3.339 |  | 25.81 | 0.6508 | 217.3107 | 25.81 | 0 | 0 | 0 | 25.81 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 190.2848 | 0 | 8.1647 | 8.1647
2025-01-06 04:00 | 1 | short_term | Short / Mid-Term Storage | 13.02 | 3.405 |  | 25.48 | 0.6524 | 222.1331 | 25.48 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 195.4372 | 0 | 8.1647 | 8.1647
2025-01-06 05:00 | 1 | short_term | Short / Mid-Term Storage | 13.23 | 3.47 |  | 25.15 | 0.6538 | 226.8803 | 25.15 | 0 | 0 | 0 | 25.15 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 200.5144 | 0 | 8.1647 | 8.1647
2025-01-06 06:00 | 1 | short_term | Short / Mid-Term Storage | 13.45 | 3.534 |  | 24.83 | 0.6552 | 231.5587 | 24.83 | 0 | 0 | 0 | 24.83 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 205.5128 | 0 | 8.1647 | 8.1647
2025-01-06 07:00 | 1 | short_term | Short / Mid-Term Storage | 13.66 | 3.598 |  | 24.51 | 0.6566 | 236.2339 | 24.51 | 0 | 0 | 0 | 24.51 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 210.508 | 0 | 8.1647 | 8.1647
2025-01-06 08:00 | 1 | short_term | Short / Mid-Term Storage | 13.87 | 3.661 |  | 24.2 | 0.6578 | 240.8371 | 24.2 | 0 | 0 | 0 | 24.2 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 215.4212 | 0 | 8.1647 | 8.1647
2025-01-06 09:00 | 1 | short_term | Short / Mid-Term Storage | 14.08 | 3.723 |  | 23.89 | 0.6591 | 245.3683 | 23.89 | 0 | 0 | 0 | 23.89 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 220.2624 | 0 | 8.1647 | 8.1647
2025-01-06 10:00 | 1 | short_term | Short / Mid-Term Storage | 14.28 | 3.784 |  | 23.58 | 0.6602 | 249.8243 | 23.58 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 225.0284 | 0 | 8.1647 | 8.1647
2025-01-06 11:00 | 1 | short_term | Short / Mid-Term Storage | 14.48 | 3.844 |  | 23.28 | 0.6613 | 254.2083 | 23.28 | 0 | 0 | 0 | 23.28 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 229.7124 | 0 | 8.1647 | 8.1647
2025-01-06 12:00 | 1 | short_term | Short / Mid-Term Storage | 14.68 | 3.904 |  | 22.98 | 0.6624 | 258.5923 | 22.98 | 0 | 0 | 0 | 22.98 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 234.3964 | 0 | 8.1647 | 8.1647
2025-01-06 13:00 | 1 | short_term | Short / Mid-Term Storage | 14.88 | 3.963 |  | 22.69 | 0.6634 | 262.9043 | 22.69 | 0 | 0 | 0 | 22.69 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 238.9984 | 0 | 8.1647 | 8.1647
2025-01-06 14:00 | 1 | short_term | Short / Mid-Term Storage | 15.07 | 4.021 |  | 22.4 | 0.6644 | 267.1411 | 22.4 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 243.5252 | 0 | 8.1647 | 8.1647
2025-01-06 15:00 | 1 | short_term | Short / Mid-Term Storage | 15.26 | 4.078 |  | 22.11 | 0.6653 | 271.3059 | 22.11 | 0 | 0 | 0 | 22.11 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 247.98 | 0 | 8.1647 | 8.1647
2025-01-06 16:00 | 1 | short_term | Short / Mid-Term Storage | 15.45 | 4.134 |  | 21.83 | 0.6662 | 275.3987 | 21.83 | 0 | 0 | 0 | 21.83 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 252.3528 | 0 | 8.1647 | 8.1647
2025-01-06 17:00 | 1 | short_term | Short / Mid-Term Storage | 15.63 | 4.189 |  | 21.56 | 0.667 | 279.4163 | 21.56 | 0 | 0 | 0 | 21.56 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 256.6404 | 0 | 8.1647 | 8.1647
2025-01-06 18:00 | 1 | short_term | Short / Mid-Term Storage | 15.81 | 4.243 |  | 21.28 | 0.6678 | 283.3619 | 21.28 | 0 | 0 | 0 | 21.28 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 260.866 | 0 | 8.1647 | 8.1647
2025-01-06 19:00 | 1 | short_term | Short / Mid-Term Storage | 15.99 | 4.296 |  | 21.02 | 0.6686 | 287.2355 | 21.02 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 264.9996 | 0 | 8.1647 | 8.1647
2025-01-06 20:00 | 1 | short_term | Short / Mid-Term Storage | 16.16 | 4.348 |  | 20.76 | 0.6694 | 291.0339 | 20.76 | 0 | 0 | 0 | 20.76 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 269.058 | 0 | 8.1647 | 8.1647
2025-01-06 21:00 | 1 | short_term | Short / Mid-Term Storage | 16.33 | 4.4 |  | 20.5 | 0.6701 | 294.8323 | 20.5 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 273.1164 | 0 | 8.1647 | 8.1647
2025-01-06 22:00 | 1 | short_term | Short / Mid-Term Storage | 16.5 | 4.45 |  | 20.25 | 0.6708 | 298.4867 | 20.25 | 0 | 0 | 0 | 20.25 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 277.0208 | 0 | 8.1647 | 8.1647
2025-01-06 23:00 | 1 | short_term | Short / Mid-Term Storage | 16.66 | 4.499 |  | 20 | 0.6714 | 302.0659 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 280.85 | 0 | 8.1647 | 8.1647
2025-01-07 | 1 | short_term | Short / Mid-Term Storage | 16.82 | 4.547 |  | 19.76 | 0.672 | 305.5731 | 19.76 | 0 | 0 | 0 | 19.76 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 284.5972 | 0 | 8.1647 | 8.1647
2025-01-07 01:00 | 1 | short_term | Short / Mid-Term Storage | 16.98 | 4.595 |  | 19.53 | 0.6726 | 309.0803 | 19.53 | 0 | 0 | 0 | 19.53 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 288.3344 | 0 | 8.1647 | 8.1647
2025-01-07 02:00 | 1 | short_term | Short / Mid-Term Storage | 17.14 | 4.641 |  | 19.3 | 0.6732 | 312.4435 | 19.3 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 291.9276 | 0 | 8.1647 | 8.1647
2025-01-07 03:00 | 1 | short_term | Short / Mid-Term Storage | 17.29 | 4.686 |  | 19.07 | 0.6738 | 315.7315 | 19.07 | 0 | 0 | 0 | 19.07 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 295.4456 | 0 | 8.1647 | 8.1647
2025-01-07 04:00 | 1 | short_term | Short / Mid-Term Storage | 17.43 | 4.729 |  | 18.85 | 0.6743 | 318.8723 | 18.85 | 0 | 0 | 0 | 18.85 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 298.8064 | 0 | 8.1647 | 8.1647
2025-01-07 05:00 | 1 | short_term | Short / Mid-Term Storage | 17.57 | 4.772 |  | 18.64 | 0.6748 | 322.0131 | 18.64 | 0 | 0 | 0 | 18.64 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 302.1572 | 0 | 8.1647 | 8.1647
2025-01-07 06:00 | 1 | short_term | Short / Mid-Term Storage | 17.71 | 4.814 |  | 18.43 | 0.6753 | 325.0819 | 18.43 | 0 | 0 | 0 | 18.43 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 305.436 | 0 | 8.1647 | 8.1647
2025-01-07 07:00 | 1 | short_term | Short / Mid-Term Storage | 17.85 | 4.854 |  | 18.23 | 0.6757 | 328.0067 | 18.23 | 0 | 0 | 0 | 18.23 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 308.5608 | 0 | 8.1647 | 8.1647
2025-01-07 08:00 | 1 | short_term | Short / Mid-Term Storage | 17.98 | 4.894 |  | 18.03 | 0.6762 | 330.9283 | 18.03 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 311.6824 | 0 | 8.1647 | 8.1647
2025-01-07 09:00 | 1 | short_term | Short / Mid-Term Storage | 18.11 | 4.932 |  | 17.84 | 0.6766 | 333.7059 | 17.84 | 0 | 0 | 0 | 17.84 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 314.65 | 0 | 8.1647 | 8.1647
2025-01-07 10:00 | 1 | short_term | Short / Mid-Term Storage | 18.23 | 4.969 |  | 17.65 | 0.677 | 336.4083 | 17.65 | 0 | 0 | 0 | 17.65 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 317.5424 | 0 | 8.1647 | 8.1647
2025-01-07 11:00 | 1 | short_term | Short / Mid-Term Storage | 18.35 | 5.005 |  | 17.47 | 0.6774 | 339.0387 | 17.47 | 0 | 0 | 0 | 17.47 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 320.3528 | 0 | 8.1647 | 8.1647
2025-01-07 12:00 | 1 | short_term | Short / Mid-Term Storage | 18.47 | 5.04 |  | 17.3 | 0.6778 | 341.5971 | 17.3 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 323.0812 | 0 | 8.1647 | 8.1647
2025-01-07 13:00 | 1 | short_term | Short / Mid-Term Storage | 18.58 | 5.073 |  | 17.13 | 0.6781 | 344.0083 | 17.13 | 0 | 0 | 0 | 17.13 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 325.6624 | 0 | 8.1647 | 8.1647
2025-01-07 14:00 | 1 | short_term | Short / Mid-Term Storage | 18.69 | 5.106 |  | 16.97 | 0.6785 | 346.4195 | 16.97 | 0 | 0 | 0 | 16.97 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 328.2336 | 0 | 8.1647 | 8.1647
2025-01-07 15:00 | 1 | short_term | Short / Mid-Term Storage | 18.79 | 5.137 |  | 16.82 | 0.6788 | 348.6835 | 16.82 | 0 | 0 | 0 | 16.82 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 330.6476 | 0 | 8.1647 | 8.1647
2025-01-07 16:00 | 1 | short_term | Short / Mid-Term Storage | 18.89 | 5.167 |  | 16.67 | 0.6791 | 350.8755 | 16.67 | 0 | 0 | 0 | 16.67 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 332.9896 | 0 | 8.1647 | 8.1647
2025-01-07 17:00 | 1 | short_term | Short / Mid-Term Storage | 18.98 | 5.195 |  | 16.52 | 0.6793 | 352.9203 | 16.52 | 0 | 0 | 0 | 16.52 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 335.1844 | 0 | 8.1647 | 8.1647
2025-01-07 18:00 | 1 | short_term | Short / Mid-Term Storage | 19.08 | 5.223 |  | 16.39 | 0.6796 | 354.9683 | 16.39 | 0 | 0 | 0 | 16.39 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 337.3624 | 0 | 8.1647 | 8.1647
2025-01-07 19:00 | 1 | short_term | Short / Mid-Term Storage | 19.16 | 5.249 |  | 16.26 | 0.6799 | 356.8659 | 16.26 | 0 | 0 | 0 | 16.26 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 339.39 | 0 | 8.1647 | 8.1647
2025-01-07 20:00 | 1 | short_term | Short / Mid-Term Storage | 19.25 | 5.274 |  | 16.13 | 0.6801 | 358.6947 | 16.13 | 0 | 0 | 0 | 16.13 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 341.3488 | 0 | 8.1647 | 8.1647
2025-01-07 21:00 | 1 | short_term | Short / Mid-Term Storage | 19.32 | 5.297 |  | 16.01 | 0.6803 | 360.3731 | 16.01 | 0 | 0 | 0 | 16.01 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 343.1472 | 0 | 8.1647 | 8.1647
2025-01-07 22:00 | 1 | short_term | Short / Mid-Term Storage | 19.4 | 5.32 |  | 15.9 | 0.6806 | 362.0547 | 15.9 | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 344.9388 | 0 | 8.1647 | 8.1647
2025-01-07 23:00 | 1 | short_term | Short / Mid-Term Storage | 19.47 | 5.341 |  | 15.8 | 0.6808 | 363.5891 | 15.8 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 346.5732 | 0 | 8.1647 | 8.1647
2025-01-08 | 1 | short_term | Short / Mid-Term Storage | 19.54 | 5.361 |  | 15.7 | 0.6809 | 365.0515 | 15.7 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 348.1356 | 0 | 8.1647 | 8.1647
2025-01-08 01:00 | 1 | short_term | Short / Mid-Term Storage | 19.6 | 5.379 |  | 15.6 | 0.6811 | 366.3667 | 15.6 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 349.5508 | 0 | 8.1647 | 8.1647
2025-01-08 02:00 | 1 | short_term | Short / Mid-Term Storage | 19.65 | 5.396 |  | 15.52 | 0.6813 | 367.6067 | 15.52 | 0 | 0 | 0 | 15.52 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 350.8708 | 0 | 8.1647 | 8.1647
2025-01-08 03:00 | 1 | short_term | Short / Mid-Term Storage | 19.71 | 5.412 |  | 15.44 | 0.6814 | 368.7779 | 15.44 | 0 | 0 | 0 | 15.44 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 352.122 | 0 | 8.1647 | 8.1647
2025-01-08 04:00 | 1 | short_term | Short / Mid-Term Storage | 19.76 | 5.427 |  | 15.37 | 0.6815 | 369.8739 | 15.37 | 0 | 0 | 0 | 15.37 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 353.288 | 0 | 8.1647 | 8.1647
2025-01-08 05:00 | 1 | short_term | Short / Mid-Term Storage | 19.8 | 5.44 |  | 15.3 | 0.6817 | 370.8227 | 15.3 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 354.3068 | 0 | 8.1647 | 8.1647
2025-01-08 06:00 | 1 | short_term | Short / Mid-Term Storage | 19.84 | 5.452 |  | 15.24 | 0.6818 | 371.6995 | 15.24 | 0 | 0 | 0 | 15.24 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 355.2436 | 0 | 8.1647 | 8.1647
2025-01-08 07:00 | 1 | short_term | Short / Mid-Term Storage | 19.88 | 5.463 |  | 15.19 | 0.6819 | 372.5043 | 15.19 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 356.0984 | 0 | 8.1647 | 8.1647
2025-01-08 08:00 | 1 | short_term | Short / Mid-Term Storage | 19.91 | 5.472 |  | 15.14 | 0.6819 | 373.1619 | 15.14 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 356.806 | 0 | 8.1647 | 8.1647
2025-01-08 09:00 | 1 | short_term | Short / Mid-Term Storage | 19.93 | 5.48 |  | 15.1 | 0.682 | 373.7443 | 15.1 | 0 | 0 | 0 | 15.1 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 357.4284 | 0 | 8.1647 | 8.1647
2025-01-08 10:00 | 1 | short_term | Short / Mid-Term Storage | 19.96 | 5.487 |  | 15.07 | 0.6821 | 374.2579 | 15.07 | 0 | 0 | 0 | 15.07 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 357.972 | 0 | 8.1647 | 8.1647
2025-01-08 11:00 | 1 | short_term | Short / Mid-Term Storage | 19.97 | 5.492 |  | 15.04 | 0.6821 | 374.6211 | 15.04 | 0 | 0 | 0 | 15.04 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.3652 | 0 | 8.1647 | 8.1647
2025-01-08 12:00 | 1 | short_term | Short / Mid-Term Storage | 19.99 | 5.496 |  | 15.02 | 0.6822 | 374.9155 | 15.02 | 0 | 0 | 0 | 15.02 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.6796 | 0 | 8.1647 | 8.1647
2025-01-08 13:00 | 1 | short_term | Short / Mid-Term Storage | 19.99 | 5.498 |  | 15.01 | 0.6822 | 375.0595 | 15.01 | 0 | 0 | 0 | 15.01 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.8336 | 0 | 8.1647 | 8.1647
2025-01-08 14:00 | 1 | short_term | Short / Mid-Term Storage | 20 | 5.5 |  | 15 | 0.6822 | 375.2067 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.9908 | 0 | 8.1647 | 8.1647
2025-01-08 15:00 | 1 | short_term | Short / Mid-Term Storage | 20 | 5.5 |  | 15 | 0.6822 | 375.2067 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.9908 | 0 | 8.1647 | 8.1647
2025-01-08 16:00 | 1 | short_term | Short / Mid-Term Storage | 19.99 | 5.498 |  | 15.01 | 0.6822 | 375.0595 | 15.01 | 0 | 0 | 0 | 15.01 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.8336 | 0 | 8.1647 | 8.1647
2025-01-08 17:00 | 1 | short_term | Short / Mid-Term Storage | 19.99 | 5.496 |  | 15.02 | 0.6822 | 374.9155 | 15.02 | 0 | 0 | 0 | 15.02 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.6796 | 0 | 8.1647 | 8.1647
2025-01-08 18:00 | 1 | short_term | Short / Mid-Term Storage | 19.97 | 5.492 |  | 15.04 | 0.6821 | 374.6211 | 15.04 | 0 | 0 | 0 | 15.04 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 358.3652 | 0 | 8.1647 | 8.1647
2025-01-08 19:00 | 1 | short_term | Short / Mid-Term Storage | 19.96 | 5.487 |  | 15.07 | 0.6821 | 374.2579 | 15.07 | 0 | 0 | 0 | 15.07 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 357.972 | 0 | 8.1647 | 8.1647
2025-01-08 20:00 | 1 | short_term | Short / Mid-Term Storage | 19.93 | 5.48 |  | 15.1 | 0.682 | 373.7443 | 15.1 | 0 | 0 | 0 | 15.1 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 357.4284 | 0 | 8.1647 | 8.1647
2025-01-08 21:00 | 1 | short_term | Short / Mid-Term Storage | 19.91 | 5.472 |  | 15.14 | 0.6819 | 373.1619 | 15.14 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 356.806 | 0 | 8.1647 | 8.1647
2025-01-08 22:00 | 1 | short_term | Short / Mid-Term Storage | 19.88 | 5.463 |  | 15.19 | 0.6819 | 372.5043 | 15.19 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 356.0984 | 0 | 8.1647 | 8.1647
2025-01-08 23:00 | 1 | short_term | Short / Mid-Term Storage | 19.84 | 5.452 |  | 15.24 | 0.6818 | 371.6995 | 15.24 | 0 | 0 | 0 | 15.24 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 355.2436 | 0 | 8.1647 | 8.1647
2025-01-09 | 1 | short_term | Short / Mid-Term Storage | 19.8 | 5.44 |  | 15.3 | 0.6817 | 370.8227 | 15.3 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 354.3068 | 0 | 8.1647 | 8.1647
2025-01-09 01:00 | 1 | short_term | Short / Mid-Term Storage | 19.76 | 5.427 |  | 15.37 | 0.6815 | 369.8739 | 15.37 | 0 | 0 | 0 | 15.37 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 353.288 | 0 | 8.1647 | 8.1647
2025-01-09 02:00 | 1 | short_term | Short / Mid-Term Storage | 19.71 | 5.412 |  | 15.44 | 0.6814 | 368.7779 | 15.44 | 0 | 0 | 0 | 15.44 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 352.122 | 0 | 8.1647 | 8.1647
2025-01-09 03:00 | 1 | short_term | Short / Mid-Term Storage | 19.65 | 5.396 |  | 15.52 | 0.6813 | 367.6067 | 15.52 | 0 | 0 | 0 | 15.52 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 350.8708 | 0 | 8.1647 | 8.1647
2025-01-09 04:00 | 1 | short_term | Short / Mid-Term Storage | 19.6 | 5.379 |  | 15.6 | 0.6811 | 366.3667 | 15.6 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 349.5508 | 0 | 8.1647 | 8.1647
2025-01-09 05:00 | 1 | short_term | Short / Mid-Term Storage | 19.54 | 5.361 |  | 15.7 | 0.6809 | 365.0515 | 15.7 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 348.1356 | 0 | 8.1647 | 8.1647
2025-01-09 06:00 | 1 | short_term | Short / Mid-Term Storage | 19.47 | 5.341 |  | 15.8 | 0.6808 | 363.5891 | 15.8 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 346.5732 | 0 | 8.1647 | 8.1647
2025-01-09 07:00 | 1 | short_term | Short / Mid-Term Storage | 19.4 | 5.32 |  | 15.9 | 0.6806 | 362.0547 | 15.9 | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 344.9388 | 0 | 8.1647 | 8.1647
2025-01-09 08:00 | 1 | short_term | Short / Mid-Term Storage | 19.32 | 5.297 |  | 16.01 | 0.6803 | 360.3731 | 16.01 | 0 | 0 | 0 | 16.01 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 343.1472 | 0 | 8.1647 | 8.1647
2025-01-09 09:00 | 1 | short_term | Short / Mid-Term Storage | 19.25 | 5.274 |  | 16.13 | 0.6801 | 358.6947 | 16.13 | 0 | 0 | 0 | 16.13 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 341.3488 | 0 | 8.1647 | 8.1647
2025-01-09 10:00 | 1 | short_term | Short / Mid-Term Storage | 19.16 | 5.249 |  | 16.26 | 0.6799 | 356.8659 | 16.26 | 0 | 0 | 0 | 16.26 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 339.39 | 0 | 8.1647 | 8.1647
2025-01-09 11:00 | 1 | short_term | Short / Mid-Term Storage | 19.08 | 5.223 |  | 16.39 | 0.6796 | 354.9683 | 16.39 | 0 | 0 | 0 | 16.39 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 337.3624 | 0 | 8.1647 | 8.1647
2025-01-09 12:00 | 1 | short_term | Short / Mid-Term Storage | 18.98 | 5.195 |  | 16.52 | 0.6793 | 352.9203 | 16.52 | 0 | 0 | 0 | 16.52 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 335.1844 | 0 | 8.1647 | 8.1647
2025-01-09 13:00 | 1 | short_term | Short / Mid-Term Storage | 18.89 | 5.167 |  | 16.67 | 0.6791 | 350.8755 | 16.67 | 0 | 0 | 0 | 16.67 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 332.9896 | 0 | 8.1647 | 8.1647
2025-01-09 14:00 | 1 | short_term | Short / Mid-Term Storage | 18.79 | 5.137 |  | 16.82 | 0.6788 | 348.6835 | 16.82 | 0 | 0 | 0 | 16.82 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 330.6476 | 0 | 8.1647 | 8.1647
2025-01-09 15:00 | 1 | short_term | Short / Mid-Term Storage | 18.69 | 5.106 |  | 16.97 | 0.6785 | 346.4195 | 16.97 | 0 | 0 | 0 | 16.97 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 328.2336 | 0 | 8.1647 | 8.1647
2025-01-09 16:00 | 1 | short_term | Short / Mid-Term Storage | 18.58 | 5.073 |  | 17.13 | 0.6781 | 344.0083 | 17.13 | 0 | 0 | 0 | 17.13 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 325.6624 | 0 | 8.1647 | 8.1647
2025-01-09 17:00 | 1 | short_term | Short / Mid-Term Storage | 18.47 | 5.04 |  | 17.3 | 0.6778 | 341.5971 | 17.3 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 323.0812 | 0 | 8.1647 | 8.1647
2025-01-09 18:00 | 1 | short_term | Short / Mid-Term Storage | 18.35 | 5.005 |  | 17.47 | 0.6774 | 339.0387 | 17.47 | 0 | 0 | 0 | 17.47 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 320.3528 | 0 | 8.1647 | 8.1647
2025-01-09 19:00 | 1 | short_term | Short / Mid-Term Storage | 18.23 | 4.969 |  | 17.65 | 0.677 | 336.4083 | 17.65 | 0 | 0 | 0 | 17.65 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 317.5424 | 0 | 8.1647 | 8.1647
2025-01-09 20:00 | 1 | short_term | Short / Mid-Term Storage | 18.11 | 4.932 |  | 17.84 | 0.6766 | 333.7059 | 17.84 | 0 | 0 | 0 | 17.84 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 314.65 | 0 | 8.1647 | 8.1647
2025-01-09 21:00 | 1 | short_term | Short / Mid-Term Storage | 17.98 | 4.894 |  | 18.03 | 0.6762 | 330.9283 | 18.03 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 311.6824 | 0 | 8.1647 | 8.1647
2025-01-09 22:00 | 1 | short_term | Short / Mid-Term Storage | 17.85 | 4.854 |  | 18.23 | 0.6757 | 328.0067 | 18.23 | 0 | 0 | 0 | 18.23 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 308.5608 | 0 | 8.1647 | 8.1647
2025-01-09 23:00 | 1 | short_term | Short / Mid-Term Storage | 17.71 | 4.814 |  | 18.43 | 0.6753 | 325.0819 | 18.43 | 0 | 0 | 0 | 18.43 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 305.436 | 0 | 8.1647 | 8.1647
2025-01-10 | 1 | short_term | Short / Mid-Term Storage | 17.57 | 4.772 |  | 18.64 | 0.6748 | 322.0131 | 18.64 | 0 | 0 | 0 | 18.64 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 302.1572 | 0 | 8.1647 | 8.1647
2025-01-10 01:00 | 1 | short_term | Short / Mid-Term Storage | 17.43 | 4.729 |  | 18.85 | 0.6743 | 318.8723 | 18.85 | 0 | 0 | 0 | 18.85 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 298.8064 | 0 | 8.1647 | 8.1647
2025-01-10 02:00 | 1 | short_term | Short / Mid-Term Storage | 17.29 | 4.686 |  | 19.07 | 0.6738 | 315.7315 | 19.07 | 0 | 0 | 0 | 19.07 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 295.4456 | 0 | 8.1647 | 8.1647
2025-01-10 03:00 | 1 | short_term | Short / Mid-Term Storage | 17.14 | 4.641 |  | 19.3 | 0.6732 | 312.4435 | 19.3 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 291.9276 | 0 | 8.1647 | 8.1647
2025-01-10 04:00 | 1 | short_term | Short / Mid-Term Storage | 16.98 | 4.595 |  | 19.53 | 0.6726 | 309.0803 | 19.53 | 0 | 0 | 0 | 19.53 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 288.3344 | 0 | 8.1647 | 8.1647
2025-01-10 05:00 | 1 | short_term | Short / Mid-Term Storage | 16.82 | 4.547 |  | 19.76 | 0.672 | 305.5731 | 19.76 | 0 | 0 | 0 | 19.76 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 284.5972 | 0 | 8.1647 | 8.1647
2025-01-10 06:00 | 1 | short_term | Short / Mid-Term Storage | 16.66 | 4.499 |  | 20 | 0.6714 | 302.0659 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 280.85 | 0 | 8.1647 | 8.1647
2025-01-10 07:00 | 1 | short_term | Short / Mid-Term Storage | 16.5 | 4.45 |  | 20.25 | 0.6708 | 298.4867 | 20.25 | 0 | 0 | 0 | 20.25 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 277.0208 | 0 | 8.1647 | 8.1647
2025-01-10 08:00 | 1 | short_term | Short / Mid-Term Storage | 16.33 | 4.4 |  | 20.5 | 0.6701 | 294.8323 | 20.5 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 273.1164 | 0 | 8.1647 | 8.1647
2025-01-10 09:00 | 1 | short_term | Short / Mid-Term Storage | 16.16 | 4.348 |  | 20.76 | 0.6694 | 291.0339 | 20.76 | 0 | 0 | 0 | 20.76 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 269.058 | 0 | 8.1647 | 8.1647
2025-01-10 10:00 | 1 | short_term | Short / Mid-Term Storage | 15.99 | 4.296 |  | 21.02 | 0.6686 | 287.2355 | 21.02 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 264.9996 | 0 | 8.1647 | 8.1647
2025-01-10 11:00 | 1 | short_term | Short / Mid-Term Storage | 15.81 | 4.243 |  | 21.28 | 0.6678 | 283.3619 | 21.28 | 0 | 0 | 0 | 21.28 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 260.866 | 0 | 8.1647 | 8.1647
2025-01-10 12:00 | 1 | short_term | Short / Mid-Term Storage | 15.63 | 4.189 |  | 21.56 | 0.667 | 279.4163 | 21.56 | 0 | 0 | 0 | 21.56 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 256.6404 | 0 | 8.1647 | 8.1647
2025-01-10 13:00 | 1 | short_term | Short / Mid-Term Storage | 15.45 | 4.134 |  | 21.83 | 0.6662 | 275.3987 | 21.83 | 0 | 0 | 0 | 21.83 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 252.3528 | 0 | 8.1647 | 8.1647
2025-01-10 14:00 | 1 | short_term | Short / Mid-Term Storage | 15.26 | 4.078 |  | 22.11 | 0.6653 | 271.3059 | 22.11 | 0 | 0 | 0 | 22.11 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 247.98 | 0 | 8.1647 | 8.1647
2025-01-10 15:00 | 1 | short_term | Short / Mid-Term Storage | 15.07 | 4.021 |  | 22.4 | 0.6644 | 267.1411 | 22.4 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 243.5252 | 0 | 8.1647 | 8.1647
2025-01-10 16:00 | 1 | short_term | Short / Mid-Term Storage | 14.88 | 3.963 |  | 22.69 | 0.6634 | 262.9043 | 22.69 | 0 | 0 | 0 | 22.69 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 238.9984 | 0 | 8.1647 | 8.1647
2025-01-10 17:00 | 1 | short_term | Short / Mid-Term Storage | 14.68 | 3.904 |  | 22.98 | 0.6624 | 258.5923 | 22.98 | 0 | 0 | 0 | 22.98 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 234.3964 | 0 | 8.1647 | 8.1647
2025-01-10 18:00 | 1 | short_term | Short / Mid-Term Storage | 14.48 | 3.844 |  | 23.28 | 0.6613 | 254.2083 | 23.28 | 0 | 0 | 0 | 23.28 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 229.7124 | 0 | 8.1647 | 8.1647
2025-01-10 19:00 | 1 | short_term | Short / Mid-Term Storage | 14.28 | 3.784 |  | 23.58 | 0.6602 | 249.8243 | 23.58 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 225.0284 | 0 | 8.1647 | 8.1647
2025-01-10 20:00 | 1 | short_term | Short / Mid-Term Storage | 14.08 | 3.723 |  | 23.89 | 0.6591 | 245.3683 | 23.89 | 0 | 0 | 0 | 23.89 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 220.2624 | 0 | 8.1647 | 8.1647
2025-01-10 21:00 | 1 | short_term | Short / Mid-Term Storage | 13.87 | 3.661 |  | 24.2 | 0.6578 | 240.8371 | 24.2 | 0 | 0 | 0 | 24.2 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 215.4212 | 0 | 8.1647 | 8.1647
2025-01-10 22:00 | 1 | short_term | Short / Mid-Term Storage | 13.66 | 3.598 |  | 24.51 | 0.6566 | 236.2339 | 24.51 | 0 | 0 | 0 | 24.51 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 210.508 | 0 | 8.1647 | 8.1647
2025-01-10 23:00 | 1 | short_term | Short / Mid-Term Storage | 13.45 | 3.534 |  | 24.83 | 0.6552 | 231.5587 | 24.83 | 0 | 0 | 0 | 24.83 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 205.5128 | 0 | 8.1647 | 8.1647
2025-01-11 | 1 | short_term | Short / Mid-Term Storage | 13.23 | 3.47 |  | 25.15 | 0.6538 | 226.8803 | 25.15 | 0 | 0 | 0 | 25.15 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 200.5144 | 0 | 8.1647 | 8.1647
2025-01-11 01:00 | 1 | short_term | Short / Mid-Term Storage | 13.02 | 3.405 |  | 25.48 | 0.6524 | 222.1331 | 25.48 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 195.4372 | 0 | 8.1647 | 8.1647
2025-01-11 02:00 | 1 | short_term | Short / Mid-Term Storage | 12.8 | 3.339 |  | 25.81 | 0.6508 | 217.3107 | 25.81 | 0 | 0 | 0 | 25.81 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 190.2848 | 0 | 8.1647 | 8.1647
2025-01-11 03:00 | 1 | short_term | Short / Mid-Term Storage | 12.57 | 3.272 |  | 26.14 | 0.6492 | 212.4131 | 26.14 | 0 | 0 | 0 | 26.14 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 185.0572 | 0 | 8.1647 | 8.1647
2025-01-11 04:00 | 1 | short_term | Short / Mid-Term Storage | 12.35 | 3.205 |  | 26.47 | 0.6475 | 207.5187 | 26.47 | 0 | 0 | 0 | 26.47 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 179.8328 | 0 | 8.1647 | 8.1647
2025-01-11 05:00 | 1 | short_term | Short / Mid-Term Storage | 12.12 | 3.137 |  | 26.81 | 0.6457 | 202.5491 | 26.81 | 0 | 0 | 0 | 26.81 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 174.5232 | 0 | 8.1647 | 8.1647
2025-01-11 06:00 | 1 | short_term | Short / Mid-Term Storage | 11.9 | 3.069 |  | 27.16 | 0.6438 | 197.5827 | 27.16 | 0 | 0 | 0 | 27.16 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 169.2068 | 0 | 8.1647 | 8.1647
2025-01-11 07:00 | 1 | short_term | Short / Mid-Term Storage | 11.67 | 3 |  | 27.5 | 0.6418 | 192.5411 | 27.5 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 163.8252 | 0 | 8.1647 | 8.1647
2025-01-11 08:00 | 1 | short_term | Short / Mid-Term Storage | 11.43 | 2.93 |  | 27.85 | 0.6397 | 187.4243 | 27.85 | 0 | 0 | 0 | 27.85 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 158.3584 | 0 | 8.1647 | 8.1647
2025-01-11 09:00 | 1 | short_term | Short / Mid-Term Storage | 11.2 | 2.86 |  | 28.2 | 0.6374 | 182.3107 | 28.2 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 152.8948 | 0 | 8.1647 | 8.1647
2025-01-11 10:00 | 1 | short_term | Short / Mid-Term Storage | 10.96 | 2.789 |  | 28.56 | 0.6351 | 177.1219 | 28.56 | 0 | 0 | 0 | 28.56 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 147.346 | 0 | 8.1647 | 8.1647
2025-01-11 11:00 | 1 | short_term | Short / Mid-Term Storage | 10.73 | 2.718 |  | 28.91 | 0.6326 | 171.9363 | 28.91 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 141.8104 | 0 | 8.1647 | 8.1647
2025-01-11 12:00 | 1 | short_term | Short / Mid-Term Storage | 10.49 | 2.646 |  | 29.27 | 0.6299 | 166.6755 | 29.27 | 0 | 0 | 0 | 29.27 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 136.1896 | 0 | 8.1647 | 8.1647
2025-01-11 13:00 | 1 | short_term | Short / Mid-Term Storage | 10.24 | 2.573 |  | 29.63 | 0.627 | 161.3395 | 29.63 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 130.4936 | 0 | 8.1647 | 8.1647
2025-01-11 14:00 | 1 | short_term | Short / Mid-Term Storage | 10 | 2.501 |  | 30 | 0.6241 | 156.0787 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 124.8628 | 0 | 8.1647 | 8.1647
2025-01-11 15:00 | 1 | short_term | Short / Mid-Term Storage | 9.76 | 2.427 |  | 30.36 | 0.6208 | 150.6739 | 30.36 | 0 | 0 | 0 | 30.36 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 119.098 | 0 | 8.1647 | 8.1647
2025-01-11 16:00 | 1 | short_term | Short / Mid-Term Storage | 9.51 | 2.354 |  | 30.73 | 0.6174 | 145.3379 | 30.73 | 0 | 0 | 0 | 30.73 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 113.392 | 0 | 8.1647 | 8.1647
2025-01-11 17:00 | 1 | short_term | Short / Mid-Term Storage | 9.27 | 2.28 |  | 31.1 | 0.6137 | 139.9331 | 31.1 | 0 | 0 | 0 | 31.1 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 107.6172 | 0 | 8.1647 | 8.1647
2025-01-11 18:00 | 1 | short_term | Short / Mid-Term Storage | 9.02 | 2.205 |  | 31.47 | 0.6098 | 134.4531 | 31.47 | 0 | 0 | 0 | 31.47 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 101.7672 | 0 | 8.1647 | 8.1647
2025-01-11 19:00 | 1 | short_term | Short / Mid-Term Storage | 8.77 | 2.13 |  | 31.85 | 0.6055 | 128.9731 | 31.85 | 0 | 0 | 0 | 31.85 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 95.9072 | 0 | 8.1647 | 8.1647
2025-01-11 20:00 | 1 | short_term | Short / Mid-Term Storage | 8.52 | 2.055 |  | 32.22 | 0.6009 | 123.4931 | 32.22 | 0 | 0 | 0 | 32.22 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 90.0572 | 0 | 8.1647 | 8.1647
2025-01-11 21:00 | 1 | short_term | Short / Mid-Term Storage | 8.27 | 1.98 |  | 32.6 | 0.596 | 118.0131 | 32.6 | 0 | 0 | 0 | 32.6 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 84.1972 | 0 | 8.1647 | 8.1647
2025-01-11 22:00 | 1 | short_term | Short / Mid-Term Storage | 8.01 | 1.904 |  | 32.98 | 0.5906 | 112.4579 | 32.98 | 0 | 0 | 0 | 32.98 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 78.262 | 0 | 8.1647 | 8.1647
2025-01-11 23:00 | 1 | short_term | Short / Mid-Term Storage | 7.76 | 1.828 |  | 33.36 | 0.5848 | 106.9059 | 33.36 | 0 | 0 | 0 | 33.36 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 72.33 | 0 | 8.1647 | 8.1647
2025-01-12 | 1 | short_term | Short / Mid-Term Storage | 7.51 | 1.752 |  | 33.74 | 0.5785 | 101.3539 | 33.74 | 0 | 0 | 0 | 33.74 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 66.398 | 0 | 8.1647 | 8.1647
2025-01-12 01:00 | 1 | short_term | Short / Mid-Term Storage | 7.25 | 1.675 |  | 34.12 | 0.5715 | 95.7267 | 34.12 | 0 | 0 | 0 | 34.12 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 60.3908 | 0 | 8.1647 | 8.1647
2025-01-12 02:00 | 1 | short_term | Short / Mid-Term Storage | 7 | 1.599 |  | 34.51 | 0.5639 | 90.1747 | 34.51 | 0 | 0 | 0 | 34.51 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 54.4488 | 0 | 8.1647 | 8.1647
2025-01-12 03:00 | 1 | short_term | Short / Mid-Term Storage | 6.74 | 1.522 |  | 34.89 | 0.5555 | 84.5475 | 34.89 | 0 | 0 | 0 | 34.89 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 48.4416 | 0 | 8.1647 | 8.1647
2025-01-12 04:00 | 1 | short_term | Short / Mid-Term Storage | 6.48 | 1.445 |  | 35.28 | 0.5462 | 78.9203 | 35.28 | 0 | 0 | 0 | 35.28 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 42.4244 | 0 | 8.1647 | 8.1647
2025-01-12 05:00 | 1 | short_term | Short / Mid-Term Storage | 6.23 | 1.368 |  | 35.66 | 0.5358 | 73.2963 | 35.66 | 0 | 0 | 0 | 35.66 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 36.4204 | 0 | 8.1647 | 8.1647
2025-01-12 06:00 | 1 | short_term | Short / Mid-Term Storage | 5.97 | 1.29 |  | 36.05 | 0.524 | 67.5971 | 36.05 | 0 | 0 | 0 | 36.05 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 30.3312 | 0 | 8.1647 | 8.1647
2025-01-12 07:00 | 1 | short_term | Short / Mid-Term Storage | 5.71 | 1.213 |  | 36.44 | 0.5109 | 61.9699 | 36.44 | 0 | 0 | 0 | 36.44 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 24.314 | 0 | 8.1647 | 8.1647
2025-01-12 08:00 | 1 | short_term | Short / Mid-Term Storage | 5.45 | 1.136 |  | 36.82 | 0.496 | 56.3427 | 36.82 | 0 | 0 | 0 | 36.82 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 18.3068 | 0 | 8.1647 | 8.1647
2025-01-12 09:00 | 1 | short_term | Short / Mid-Term Storage | 5.19 | 1.058 |  | 37.21 | 0.4787 | 50.6435 | 37.21 | 0 | 0 | 0 | 37.21 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 12.2176 | 0 | 8.1647 | 8.1647
2025-01-12 10:00 | 1 | short_term | Short / Mid-Term Storage | 4.94 | 1 |  | 37.6 | 0.4639 | 46.3875 | 37.6 | 0 | 0 | 0 | 37.6 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 7.5716 | 0 | 8.1647 | 8.1647
2025-01-12 11:00 | 1 | short_term | Short / Mid-Term Storage | 4.68 | 1 |  | 37.98 | 0.463 | 46.3043 | 37.98 | 0 | 0 | 0 | 37.98 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 7.1084 | 0 | 8.1647 | 8.1647
2025-01-12 12:00 | 1 | short_term | Short / Mid-Term Storage | 4.42 | 1 |  | 38.37 | 0.4622 | 46.2211 | 38.37 | 0 | 0 | 0 | 38.37 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 6.6352 | 0 | 8.1647 | 8.1647
2025-01-12 13:00 | 1 | short_term | Short / Mid-Term Storage | 4.16 | 1 |  | 38.76 | 0.4614 | 46.1379 | 38.76 | 0 | 0 | 0 | 38.76 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 6.162 | 0 | 8.1647 | 8.1647
2025-01-12 14:00 | 1 | short_term | Short / Mid-Term Storage | 3.9 | 1 |  | 39.14 | 0.4605 | 46.0547 | 39.14 | 0 | 0 | 0 | 39.14 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 5.6988 | 0 | 8.1647 | 8.1647
2025-01-12 15:00 | 1 | short_term | Short / Mid-Term Storage | 3.65 | 1 |  | 39.53 | 0.4597 | 45.9747 | 39.53 | 0 | 0 | 0 | 39.53 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 5.2288 | 0 | 8.1647 | 8.1647
2025-01-12 16:00 | 1 | short_term | Short / Mid-Term Storage | 3.39 | 1 |  | 39.92 | 0.4589 | 45.8915 | 39.92 | 0 | 0 | 0 | 39.92 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 4.7556 | 0 | 8.1647 | 8.1647
2025-01-12 17:00 | 1 | short_term | Short / Mid-Term Storage | 3.13 | 1 |  | 40.3 | 0.4581 | 45.8083 | 40.3 | 0 | 0 | 0 | 40.3 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 4.2924 | 0 | 8.1647 | 8.1647
2025-01-12 18:00 | 1 | short_term | Short / Mid-Term Storage | 2.88 | 1 |  | 40.68 | 0.4573 | 45.7283 | 40.68 | 0 | 0 | 0 | 40.68 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 3.8324 | 0 | 8.1647 | 8.1647
2025-01-12 19:00 | 1 | short_term | Short / Mid-Term Storage | 2.62 | 1 |  | 41.07 | 0.4565 | 45.6451 | 41.07 | 0 | 0 | 0 | 41.07 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 3.3592 | 0 | 8.1647 | 8.1647
2025-01-12 20:00 | 1 | short_term | Short / Mid-Term Storage | 2.37 | 1 |  | 41.45 | 0.4557 | 45.5651 | 41.45 | 0 | 0 | 0 | 41.45 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 2.8992 | 0 | 8.1647 | 8.1647
2025-01-12 21:00 | 1 | short_term | Short / Mid-Term Storage | 2.11 | 1 |  | 41.83 | 0.4548 | 45.4819 | 41.83 | 0 | 0 | 0 | 41.83 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 2.436 | 0 | 8.1647 | 8.1647
2025-01-12 22:00 | 1 | short_term | Short / Mid-Term Storage | 1.86 | 1 |  | 42.21 | 0.454 | 45.4019 | 42.21 | 0 | 0 | 0 | 42.21 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 1.976 | 0 | 8.1647 | 8.1647
2025-01-12 23:00 | 1 | short_term | Short / Mid-Term Storage | 1.61 | 1 |  | 42.59 | 0.4532 | 45.3219 | 42.59 | 0 | 0 | 0 | 42.59 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 1.516 | 0 | 8.1647 | 8.1647
2025-01-13 | 1 | short_term | Short / Mid-Term Storage | 1.36 | 1 |  | 42.96 | 0.4524 | 45.2419 | 42.96 | 0 | 0 | 0 | 42.96 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 1.066 | 0 | 8.1647 | 8.1647
2025-01-13 01:00 | 1 | short_term | Short / Mid-Term Storage | 1.11 | 1 |  | 43.34 | 0.4516 | 45.1619 | 43.34 | 0 | 0 | 0 | 43.34 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 0.606 | 0 | 8.1647 | 8.1647
2025-01-13 02:00 | 1 | short_term | Short / Mid-Term Storage | 0.86 | 1 |  | 43.71 | 0.4508 | 45.0819 | 43.71 | 0 | 0 | 0 | 43.71 | 0 | 0 | 0 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 79.9791 | 2902.9508 | 1.2159 | 0 | 0 | 0 | 1.2159 | 0.156 | 0 | 8.1647 | 8.1647
2025-01-13 03:00 | 1 | short_term | Short / Mid-Term Storage | 0.61 | 1 |  | 44.08 | 0.45 | 45.0019 | 44.08 | 0 | 0 | 0 | 44.08 | 0 | 0 | 0 | 79.9791 | 79.974 | 79.9791 | 79.9791 | 79.9791 | 79.9581 | 2902.6569 | 0.9219 | 0 | 0 | 0 | 1.2158 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 04:00 | 1 | short_term | Short / Mid-Term Storage | 0.36 | 1 |  | 44.45 | 0.4492 | 44.9219 | 44.45 | 0 | 0 | 0 | 44.45 | 0 | 0 | 0 | 79.974 | 79.9612 | 79.9791 | 79.9581 | 79.9791 | 79.9372 | 2901.9133 | 0.4719 | 0 | 0 | 0 | 1.2155 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 05:00 | 1 | short_term | Short / Mid-Term Storage | 0.12 | 1 |  | 44.82 | 0.4485 | 44.8451 | 44.82 | 0 | 0 | 0 | 44.82 | 0 | 0 | 0 | 79.9612 | 79.9407 | 79.9791 | 79.9372 | 79.9616 | 79.9163 | 2900.7234 | 0.0251 | 0 | 0 | 0 | 1.215 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 06:00 | 1 | short_term | Short / Mid-Term Storage | -0.12 | 1 |  | 45.19 | 0.4477 | 44.7739 | 44.7739 | 0.4161 | 0 | 0 | 45.19 | 0 | 0 | 0 | 79.9407 | 79.9126 | 79.9616 | 79.9163 | 79.9372 | 79.8834 | 2899.093 | 0 | 0.4161 | 0 | 0.4161 | 1.2143 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 07:00 | 1 | short_term | Short / Mid-Term Storage | -0.37 | 1 |  | 45.55 | 0.447 | 44.7017 | 44.7017 | 0.8483 | 0 | 0 | 45.55 | 0 | 0 | 0 | 79.9126 | 79.8772 | 79.9372 | 79.8834 | 79.9163 | 79.7995 | 2897.0313 | 0 | 0.8483 | 0 | 0.8483 | 1.2134 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 08:00 | 1 | short_term | Short / Mid-Term Storage | -0.61 | 1 |  | 45.91 | 0.4463 | 44.6316 | 44.6316 | 1.2784 | 0 | 0 | 45.91 | 0 | 0 | 0 | 79.8772 | 79.8343 | 79.9163 | 79.7995 | 79.8767 | 79.7194 | 2894.5405 | 0 | 1.2784 | 0 | 1.2784 | 1.2124 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 09:00 | 1 | short_term | Short / Mid-Term Storage | -0.84 | 1 |  | 46.27 | 0.4457 | 44.5707 | 44.5707 | 1.6993 | 0 | 0 | 46.27 | 0 | 0 | 0 | 79.8343 | 79.7842 | 79.8767 | 79.7194 | 79.8536 | 79.6219 | 2891.63 | 0 | 1.6993 | 0 | 1.6993 | 1.2112 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 10:00 | 1 | short_term | Short / Mid-Term Storage | -1.08 | 1 |  | 46.62 | 0.445 | 44.5012 | 44.5012 | 2.1188 | 0 | 0 | 46.62 | 0 | 0 | 0 | 79.7842 | 79.7269 | 79.8536 | 79.6219 | 79.8328 | 79.5411 | 2888.3014 | 0 | 2.1188 | 0 | 2.1188 | 1.2098 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 11:00 | 1 | short_term | Short / Mid-Term Storage | -1.32 | 1 |  | 46.97 | 0.4443 | 44.4311 | 44.4311 | 2.5389 | 0 | 0 | 46.97 | 0 | 0 | 0 | 79.7269 | 79.6623 | 79.8328 | 79.5411 | 79.7924 | 79.4624 | 2884.5543 | 0 | 2.5389 | 0 | 2.5389 | 1.2082 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 12:00 | 1 | short_term | Short / Mid-Term Storage | -1.55 | 1 |  | 47.32 | 0.4437 | 44.3704 | 44.3704 | 2.9496 | 0 | 0 | 47.32 | 0 | 0 | 0 | 79.6623 | 79.5908 | 79.7924 | 79.4624 | 79.7702 | 79.3655 | 2880.3983 | 0 | 2.9496 | 0 | 2.9496 | 1.2065 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 13:00 | 1 | short_term | Short / Mid-Term Storage | -1.78 | 1 |  | 47.67 | 0.443 | 44.3039 | 44.3039 | 3.3661 | 0 | 0 | 47.67 | 0 | 0 | 0 | 79.5908 | 79.5121 | 79.7702 | 79.3655 | 79.7374 | 79.2859 | 2875.8277 | 0 | 3.3661 | 0 | 3.3661 | 1.2045 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 14:00 | 1 | short_term | Short / Mid-Term Storage | -2.01 | 1 |  | 48.02 | 0.4424 | 44.2408 | 44.2408 | 3.7792 | 0 | 0 | 48.02 | 0 | 0 | 0 | 79.5121 | 79.4263 | 79.7374 | 79.2859 | 79.6538 | 79.1963 | 2870.8461 | 0 | 3.7792 | 0 | 3.7792 | 1.2025 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 15:00 | 1 | short_term | Short / Mid-Term Storage | -2.24 | 1 |  | 48.36 | 0.4419 | 44.194 | 44.194 | 4.166 | 0 | 0 | 48.36 | 0 | 0 | 0 | 79.4263 | 79.3339 | 79.6538 | 79.1963 | 79.5739 | 79.0594 | 2865.4799 | 0 | 4.166 | 0 | 4.166 | 1.2002 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 16:00 | 1 | short_term | Short / Mid-Term Storage | -2.46 | 1 |  | 48.69 | 0.4415 | 44.1492 | 44.1492 | 4.5408 | 0 | 0 | 48.69 | 0 | 0 | 0 | 79.3339 | 79.2351 | 79.5739 | 79.0594 | 79.4766 | 78.928 | 2859.7412 | 0 | 4.5408 | 0 | 4.5408 | 1.1978 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 17:00 | 1 | short_term | Short / Mid-Term Storage | -2.69 | 1 |  | 49.03 | 0.4411 | 44.1067 | 44.1067 | 4.9233 | 0 | 0 | 49.03 | 0 | 0 | 0 | 79.2351 | 79.1298 | 79.4766 | 78.928 | 79.3961 | 78.7781 | 2853.6226 | 0 | 4.9233 | 0 | 4.9233 | 1.1952 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 18:00 | 1 | short_term | Short / Mid-Term Storage | -2.91 | 1 |  | 49.36 | 0.4406 | 44.0621 | 44.0621 | 5.2979 | 0 | 0 | 49.36 | 0 | 0 | 0 | 79.1298 | 79.0181 | 79.3961 | 78.7781 | 79.3176 | 78.646 | 2847.1322 | 0 | 5.2979 | 0 | 5.2979 | 1.1925 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 19:00 | 1 | short_term | Short / Mid-Term Storage | -3.12 | 1 |  | 49.69 | 0.4402 | 44.02 | 44.02 | 5.67 | 0 | 0 | 49.69 | 0 | 0 | 0 | 79.0181 | 78.9 | 79.3176 | 78.646 | 79.221 | 78.5163 | 2840.2725 | 0 | 5.67 | 0 | 5.67 | 1.1897 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 20:00 | 1 | short_term | Short / Mid-Term Storage | -3.34 | 1 |  | 50.01 | 0.4398 | 43.9805 | 43.9805 | 6.0295 | 0 | 0 | 50.01 | 0 | 0 | 0 | 78.9 | 78.7757 | 79.221 | 78.5163 | 79.1417 | 78.3703 | 2833.0564 | 0 | 6.0295 | 0 | 6.0295 | 1.1866 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 21:00 | 1 | short_term | Short / Mid-Term Storage | -3.55 | 1 |  | 50.33 | 0.4394 | 43.9387 | 43.9387 | 6.3913 | 0 | 0 | 50.33 | 0 | 0 | 0 | 78.7757 | 78.6453 | 79.1417 | 78.3703 | 79.0523 | 78.2412 | 2825.4816 | 0 | 6.3913 | 0 | 6.3913 | 1.1835 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 22:00 | 1 | short_term | Short / Mid-Term Storage | -3.76 | 1 |  | 50.65 | 0.439 | 43.9001 | 43.9001 | 6.7499 | 0 | 0 | 50.65 | 0 | 0 | 0 | 78.6453 | 78.5088 | 79.0523 | 78.2412 | 78.9158 | 78.1024 | 2817.5515 | 0 | 6.7499 | 0 | 6.7499 | 1.1801 | 0 | 0 | 8.1647 | 8.1647
2025-01-13 23:00 | 1 | short_term | Short / Mid-Term Storage | -3.97 | 1 |  | 50.96 | 0.4388 | 43.8765 | 43.8765 | 7.0835 | 0 | 0 | 50.96 | 0 | 0 | 0 | 78.5088 | 78.3666 | 78.9158 | 78.1024 | 78.7847 | 77.9201 | 2809.2914 | 0 | 7.0835 | 0 | 7.0835 | 1.1767 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 | 1 | short_term | Short / Mid-Term Storage | -4.18 | 1 |  | 51.27 | 0.4385 | 43.8513 | 43.8513 | 7.4187 | 0 | 0 | 51.27 | 0 | 0 | 0 | 78.3666 | 78.2186 | 78.7847 | 77.9201 | 78.6353 | 77.7429 | 2800.6996 | 0 | 7.4187 | 0 | 7.4187 | 1.1731 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 01:00 | 1 | short_term | Short / Mid-Term Storage | -4.38 | 1 |  | 51.57 | 0.4384 | 43.8351 | 43.8351 | 7.7349 | 0 | 0 | 51.57 | 0 | 0 | 0 | 78.2186 | 78.0653 | 78.6353 | 77.7429 | 78.5036 | 77.5501 | 2791.7953 | 0 | 7.7349 | 0 | 7.7349 | 1.1693 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 02:00 | 1 | short_term | Short / Mid-Term Storage | -4.58 | 1 |  | 51.87 | 0.4381 | 43.8132 | 43.8132 | 8.0568 | 0 | 0 | 51.87 | 0 | 0 | 0 | 78.0653 | 77.9066 | 78.5036 | 77.5501 | 78.3743 | 77.3741 | 2782.5731 | 0 | 8.0568 | 0 | 8.0568 | 1.1655 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 03:00 | 1 | short_term | Short / Mid-Term Storage | -4.78 | 1 |  | 52.17 | 0.4379 | 43.7906 | 43.7906 | 8.3794 | 0 | 0 | 52.17 | 0 | 0 | 0 | 77.9066 | 77.7423 | 78.3743 | 77.3741 | 78.2287 | 77.2004 | 2773.0322 | 0 | 8.3794 | 0 | 8.3794 | 1.1615 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 04:00 | 1 | short_term | Short / Mid-Term Storage | -4.97 | 1 |  | 52.46 | 0.4378 | 43.7764 | 43.7764 | 8.6836 | 0 | 0 | 52.46 | 0 | 0 | 0 | 77.7423 | 77.5729 | 78.2287 | 77.2004 | 78.1 | 77.013 | 2763.1913 | 0 | 8.6836 | 0 | 8.6836 | 1.1574 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 05:00 | 1 | short_term | Short / Mid-Term Storage | -5.16 | 1 |  | 52.75 | 0.4376 | 43.7568 | 43.7568 | 8.9932 | 0 | 0 | 52.75 | 0 | 0 | 0 | 77.5729 | 77.3982 | 78.1 | 77.013 | 77.9616 | 76.8417 | 2753.045 | 0 | 8.9932 | 0 | 8.9932 | 1.1531 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 06:00 | 1 | short_term | Short / Mid-Term Storage | -5.35 | 1 |  | 53.03 | 0.4374 | 43.7403 | 43.7403 | 9.2897 | 0 | 0 | 53.03 | 0 | 0 | 0 | 77.3982 | 77.2185 | 77.9616 | 76.8417 | 77.7799 | 76.6626 | 2742.6065 | 0 | 9.2897 | 0 | 9.2897 | 1.1487 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 07:00 | 1 | short_term | Short / Mid-Term Storage | -5.54 | 1 |  | 53.31 | 0.4374 | 43.7376 | 43.7376 | 9.5724 | 0 | 0 | 53.31 | 0 | 0 | 0 | 77.2185 | 77.034 | 77.7799 | 76.6626 | 77.6032 | 76.442 | 2731.8899 | 0 | 9.5724 | 0 | 9.5724 | 1.1443 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 08:00 | 1 | short_term | Short / Mid-Term Storage | -5.72 | 1 |  | 53.58 | 0.4374 | 43.7366 | 43.7366 | 9.8434 | 0 | 0 | 53.58 | 0 | 0 | 0 | 77.034 | 76.8449 | 77.6032 | 76.442 | 77.4109 | 76.2281 | 2720.9068 | 0 | 9.8434 | 0 | 9.8434 | 1.1397 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 09:00 | 1 | short_term | Short / Mid-Term Storage | -5.9 | 1 |  | 53.85 | 0.4374 | 43.7405 | 43.7405 | 10.1095 | 0 | 0 | 53.85 | 0 | 0 | 0 | 76.8449 | 76.6513 | 77.4109 | 76.2281 | 77.2354 | 75.9992 | 2709.6624 | 0 | 10.1095 | 0 | 10.1095 | 1.1349 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 10:00 | 1 | short_term | Short / Mid-Term Storage | -6.07 | 1 |  | 54.11 | 0.4374 | 43.7423 | 43.7423 | 10.3677 | 0 | 0 | 54.11 | 0 | 0 | 0 | 76.6513 | 76.4533 | 77.2354 | 75.9992 | 77.0623 | 75.7882 | 2698.1645 | 0 | 10.3677 | 0 | 10.3677 | 1.1301 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 11:00 | 1 | short_term | Short / Mid-Term Storage | -6.25 | 1 |  | 54.37 | 0.4374 | 43.7401 | 43.7401 | 10.6299 | 0 | 0 | 54.37 | 0 | 0 | 0 | 76.4533 | 76.251 | 77.0623 | 75.7882 | 76.8754 | 75.5791 | 2686.4094 | 0 | 10.6299 | 0 | 10.6299 | 1.1252 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 12:00 | 1 | short_term | Short / Mid-Term Storage | -6.42 | 1 |  | 54.62 | 0.4375 | 43.7455 | 43.7455 | 10.8745 | 0 | 0 | 54.62 | 0 | 0 | 0 | 76.251 | 76.0444 | 76.8754 | 75.5791 | 76.7046 | 75.3586 | 2674.4147 | 0 | 10.8745 | 0 | 10.8745 | 1.1202 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 13:00 | 1 | short_term | Short / Mid-Term Storage | -6.58 | 1 |  | 54.87 | 0.4375 | 43.7489 | 43.7489 | 11.1211 | 0 | 0 | 54.87 | 0 | 0 | 0 | 76.0444 | 75.8338 | 76.7046 | 75.3586 | 76.526 | 75.1539 | 2662.1786 | 0 | 11.1211 | 0 | 11.1211 | 1.1151 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 14:00 | 1 | short_term | Short / Mid-Term Storage | -6.74 | 1 |  | 55.12 | 0.4375 | 43.7549 | 43.7549 | 11.3651 | 0 | 0 | 55.12 | 0 | 0 | 0 | 75.8338 | 75.619 | 76.526 | 75.1539 | 76.306 | 74.9418 | 2649.7036 | 0 | 11.3651 | 0 | 11.3651 | 1.1098 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 15:00 | 1 | short_term | Short / Mid-Term Storage | -6.9 | 1 |  | 55.36 | 0.4377 | 43.7741 | 43.7741 | 11.5859 | 0 | 0 | 55.36 | 0 | 0 | 0 | 75.619 | 75.4005 | 76.306 | 74.9418 | 76.0928 | 74.6915 | 2637.0132 | 0 | 11.5859 | 0 | 11.5859 | 1.1045 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 16:00 | 1 | short_term | Short / Mid-Term Storage | -7.06 | 1 |  | 55.59 | 0.4379 | 43.7911 | 43.7911 | 11.7989 | 0 | 0 | 55.59 | 0 | 0 | 0 | 75.4005 | 75.1785 | 76.0928 | 74.6915 | 75.8646 | 74.449 | 2624.1152 | 0 | 11.7989 | 0 | 11.7989 | 1.0991 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 17:00 | 1 | short_term | Short / Mid-Term Storage | -7.21 | 1 |  | 55.82 | 0.4382 | 43.8161 | 43.8161 | 12.0039 | 0 | 0 | 55.82 | 0 | 0 | 0 | 75.1785 | 74.953 | 75.8646 | 74.449 | 75.6542 | 74.1927 | 2611.0177 | 0 | 12.0039 | 0 | 12.0039 | 1.0936 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 18:00 | 1 | short_term | Short / Mid-Term Storage | -7.36 | 1 |  | 56.04 | 0.4384 | 43.8354 | 43.8354 | 12.2046 | 0 | 0 | 56.04 | 0 | 0 | 0 | 74.953 | 74.7241 | 75.6542 | 74.1927 | 75.4457 | 73.9548 | 2597.7251 | 0 | 12.2046 | 0 | 12.2046 | 1.0881 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 19:00 | 1 | short_term | Short / Mid-Term Storage | -7.5 | 1 |  | 56.26 | 0.4386 | 43.8574 | 43.8574 | 12.4026 | 0 | 0 | 56.26 | 0 | 0 | 0 | 74.7241 | 74.4919 | 75.4457 | 73.9548 | 75.2258 | 73.7191 | 2584.24 | 0 | 12.4026 | 0 | 12.4026 | 1.0824 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 20:00 | 1 | short_term | Short / Mid-Term Storage | -7.64 | 1 |  | 56.47 | 0.4388 | 43.8829 | 43.8829 | 12.5871 | 0 | 0 | 56.47 | 0 | 0 | 0 | 74.4919 | 74.2567 | 75.2258 | 73.7191 | 75.0218 | 73.474 | 2570.5763 | 0 | 12.5871 | 0 | 12.5871 | 1.0767 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 21:00 | 1 | short_term | Short / Mid-Term Storage | -7.78 | 1 |  | 56.67 | 0.439 | 43.9034 | 43.9034 | 12.7666 | 0 | 0 | 56.67 | 0 | 0 | 0 | 74.2567 | 74.0185 | 75.0218 | 73.474 | 74.8103 | 73.2453 | 2556.7388 | 0 | 12.7666 | 0 | 12.7666 | 1.0709 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 22:00 | 1 | short_term | Short / Mid-Term Storage | -7.91 | 1 |  | 56.87 | 0.4393 | 43.9295 | 43.9295 | 12.9405 | 0 | 0 | 56.87 | 0 | 0 | 0 | 74.0185 | 73.7773 | 74.8103 | 73.2453 | 74.5607 | 73.0099 | 2542.7333 | 0 | 12.9405 | 0 | 12.9405 | 1.065 | 0 | 0 | 8.1647 | 8.1647
2025-01-14 23:00 | 1 | short_term | Short / Mid-Term Storage | -8.04 | 1 |  | 57.07 | 0.4397 | 43.9678 | 43.9678 | 13.1022 | 0 | 0 | 57.07 | 0 | 0 | 0 | 73.7773 | 73.5335 | 74.5607 | 73.0099 | 74.3189 | 72.7382 | 2528.572 | 0 | 13.1022 | 0 | 13.1022 | 1.0591 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 | 1 | short_term | Short / Mid-Term Storage | -8.17 | 1 |  | 57.25 | 0.44 | 44.0035 | 44.0035 | 13.2465 | 0 | 0 | 57.25 | 0 | 0 | 0 | 73.5335 | 73.2873 | 74.3189 | 72.7382 | 74.0634 | 72.4767 | 2514.2724 | 0 | 13.2465 | 0 | 13.2465 | 1.0531 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 01:00 | 1 | short_term | Short / Mid-Term Storage | -8.29 | 1 |  | 57.44 | 0.4405 | 44.0469 | 44.0469 | 13.3931 | 0 | 0 | 57.44 | 0 | 0 | 0 | 73.2873 | 73.0387 | 74.0634 | 72.4767 | 73.8262 | 72.201 | 2499.8323 | 0 | 13.3931 | 0 | 13.3931 | 1.0471 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 02:00 | 1 | short_term | Short / Mid-Term Storage | -8.41 | 1 |  | 57.61 | 0.4408 | 44.0844 | 44.0844 | 13.5256 | 0 | 0 | 57.61 | 0 | 0 | 0 | 73.0387 | 72.7879 | 73.8262 | 72.201 | 73.5911 | 71.9457 | 2485.2657 | 0 | 13.5256 | 0 | 13.5256 | 1.041 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 03:00 | 1 | short_term | Short / Mid-Term Storage | -8.52 | 1 |  | 57.78 | 0.4412 | 44.1244 | 44.1244 | 13.6556 | 0 | 0 | 57.78 | 0 | 0 | 0 | 72.7879 | 72.535 | 73.5911 | 71.9457 | 73.3467 | 71.6928 | 2470.5754 | 0 | 13.6556 | 0 | 13.6556 | 1.0348 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 04:00 | 1 | short_term | Short / Mid-Term Storage | -8.63 | 1 |  | 57.95 | 0.4417 | 44.1675 | 44.1675 | 13.7825 | 0 | 0 | 57.95 | 0 | 0 | 0 | 72.535 | 72.28 | 73.3467 | 71.6928 | 73.1187 | 71.431 | 2455.7642 | 0 | 13.7825 | 0 | 13.7825 | 1.0286 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 05:00 | 1 | short_term | Short / Mid-Term Storage | -8.74 | 1 |  | 58.11 | 0.4421 | 44.2052 | 44.2052 | 13.9048 | 0 | 0 | 58.11 | 0 | 0 | 0 | 72.28 | 72.023 | 73.1187 | 71.431 | 72.884 | 71.1863 | 2440.8371 | 0 | 13.9048 | 0 | 13.9048 | 1.0223 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 06:00 | 1 | short_term | Short / Mid-Term Storage | -8.84 | 1 |  | 58.26 | 0.4425 | 44.2483 | 44.2483 | 14.0117 | 0 | 0 | 58.26 | 0 | 0 | 0 | 72.023 | 71.7643 | 72.884 | 71.1863 | 72.6131 | 70.937 | 2425.8094 | 0 | 14.0117 | 0 | 14.0117 | 1.0161 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 07:00 | 1 | short_term | Short / Mid-Term Storage | -8.94 | 1 |  | 58.41 | 0.443 | 44.303 | 44.303 | 14.107 | 0 | 0 | 58.41 | 0 | 0 | 0 | 71.7643 | 71.504 | 72.6131 | 70.937 | 72.3523 | 70.6531 | 2410.6926 | 0 | 14.107 | 0 | 14.107 | 1.0097 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 08:00 | 1 | short_term | Short / Mid-Term Storage | -9.03 | 1 |  | 58.55 | 0.4436 | 44.3577 | 44.3577 | 14.1923 | 0 | 0 | 58.55 | 0 | 0 | 0 | 71.504 | 71.2424 | 72.3523 | 70.6531 | 72.0775 | 70.3807 | 2395.4969 | 0 | 14.1923 | 0 | 14.1923 | 1.0034 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 09:00 | 1 | short_term | Short / Mid-Term Storage | -9.12 | 1 |  | 58.68 | 0.4442 | 44.4168 | 44.4168 | 14.2632 | 0 | 0 | 58.68 | 0 | 0 | 0 | 71.2424 | 70.9797 | 72.0775 | 70.3807 | 71.8229 | 70.0962 | 2380.2368 | 0 | 14.2632 | 0 | 14.2632 | 0.997 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 10:00 | 1 | short_term | Short / Mid-Term Storage | -9.2 | 1 |  | 58.81 | 0.4447 | 44.4727 | 44.4727 | 14.3373 | 0 | 0 | 58.81 | 0 | 0 | 0 | 70.9797 | 70.7158 | 71.8229 | 70.0962 | 71.5708 | 69.8315 | 2364.9089 | 0 | 14.3373 | 0 | 14.3373 | 0.9905 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 11:00 | 1 | short_term | Short / Mid-Term Storage | -9.29 | 1 |  | 58.93 | 0.4452 | 44.5245 | 44.5245 | 14.4055 | 0 | 0 | 58.93 | 0 | 0 | 0 | 70.7158 | 70.4508 | 71.5708 | 69.8315 | 71.3098 | 69.5701 | 2349.5193 | 0 | 14.4055 | 0 | 14.4055 | 0.9841 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 12:00 | 1 | short_term | Short / Mid-Term Storage | -9.36 | 1 |  | 59.04 | 0.4459 | 44.5857 | 44.5857 | 14.4543 | 0 | 0 | 59.04 | 0 | 0 | 0 | 70.4508 | 70.1851 | 71.3098 | 69.5701 | 71.0657 | 69.3025 | 2334.0874 | 0 | 14.4543 | 0 | 14.4543 | 0.9776 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 13:00 | 1 | short_term | Short / Mid-Term Storage | -9.43 | 1 |  | 59.15 | 0.4464 | 44.6414 | 44.6414 | 14.5086 | 0 | 0 | 59.15 | 0 | 0 | 0 | 70.1851 | 69.9186 | 71.0657 | 69.3025 | 70.8172 | 69.0511 | 2318.6076 | 0 | 14.5086 | 0 | 14.5086 | 0.9712 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 14:00 | 1 | short_term | Short / Mid-Term Storage | -9.5 | 1 |  | 59.25 | 0.447 | 44.6985 | 44.6985 | 14.5515 | 0 | 0 | 59.25 | 0 | 0 | 0 | 69.9186 | 69.6515 | 70.8172 | 69.0511 | 70.5341 | 68.7967 | 2303.0914 | 0 | 14.5515 | 0 | 14.5515 | 0.9647 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 15:00 | 1 | short_term | Short / Mid-Term Storage | -9.57 | 1 |  | 59.35 | 0.4477 | 44.7667 | 44.7667 | 14.5833 | 0 | 0 | 59.35 | 0 | 0 | 0 | 69.6515 | 69.3839 | 70.5341 | 68.7967 | 70.2625 | 68.5094 | 2287.55 | 0 | 14.5833 | 0 | 14.5833 | 0.9581 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 16:00 | 1 | short_term | Short / Mid-Term Storage | -9.63 | 1 |  | 59.44 | 0.4483 | 44.8344 | 44.8344 | 14.6056 | 0 | 0 | 59.44 | 0 | 0 | 0 | 69.3839 | 69.1161 | 70.2625 | 68.5094 | 69.9788 | 68.2348 | 2271.9927 | 0 | 14.6056 | 0 | 14.6056 | 0.9516 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 17:00 | 1 | short_term | Short / Mid-Term Storage | -9.68 | 1 |  | 59.52 | 0.4491 | 44.9092 | 44.9092 | 14.6108 | 0 | 0 | 59.52 | 0 | 0 | 0 | 69.1161 | 68.8483 | 69.9788 | 68.2348 | 69.7149 | 67.9505 | 2256.4368 | 0 | 14.6108 | 0 | 14.6108 | 0.9451 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 18:00 | 1 | short_term | Short / Mid-Term Storage | -9.73 | 1 |  | 59.6 | 0.4498 | 44.9776 | 44.9776 | 14.6224 | 0 | 0 | 59.6 | 0 | 0 | 0 | 68.8483 | 68.5804 | 69.7149 | 67.9505 | 69.4543 | 67.6851 | 2240.8758 | 0 | 14.6224 | 0 | 14.6224 | 0.9386 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 19:00 | 1 | short_term | Short / Mid-Term Storage | -9.78 | 1 |  | 59.67 | 0.4505 | 45.045 | 45.045 | 14.625 | 0 | 0 | 59.67 | 0 | 0 | 0 | 68.5804 | 68.3125 | 69.4543 | 67.6851 | 69.1874 | 67.4243 | 2225.3188 | 0 | 14.625 | 0 | 14.625 | 0.9321 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 20:00 | 1 | short_term | Short / Mid-Term Storage | -9.82 | 1 |  | 59.73 | 0.4512 | 45.1176 | 45.1176 | 14.6124 | 0 | 0 | 59.73 | 0 | 0 | 0 | 68.3125 | 68.045 | 69.1874 | 67.4243 | 68.9368 | 67.1593 | 2209.7808 | 0 | 14.6124 | 0 | 14.6124 | 0.9256 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 21:00 | 1 | short_term | Short / Mid-Term Storage | -9.86 | 1 |  | 59.79 | 0.4519 | 45.185 | 45.185 | 14.605 | 0 | 0 | 59.79 | 0 | 0 | 0 | 68.045 | 67.7777 | 68.9368 | 67.1593 | 68.6831 | 66.9097 | 2194.2568 | 0 | 14.605 | 0 | 14.605 | 0.9191 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 22:00 | 1 | short_term | Short / Mid-Term Storage | -9.89 | 1 |  | 59.84 | 0.4526 | 45.2566 | 45.2566 | 14.5834 | 0 | 0 | 59.84 | 0 | 0 | 0 | 67.7777 | 67.5109 | 68.6831 | 66.9097 | 68.3966 | 66.6592 | 2178.7608 | 0 | 14.5834 | 0 | 14.5834 | 0.9126 | 0 | 0 | 8.1647 | 8.1647
2025-01-15 23:00 | 1 | short_term | Short / Mid-Term Storage | -9.92 | 1 |  | 59.88 | 0.4534 | 45.3387 | 45.3387 | 14.5413 | 0 | 0 | 59.88 | 0 | 0 | 0 | 67.5109 | 67.245 | 68.3966 | 66.6592 | 68.1229 | 66.3786 | 2163.3134 | 0 | 14.5413 | 0 | 14.5413 | 0.9061 | 0 | 0 | 8.1647 | 8.1647
2025-01-16 | 1 | short_term | Short / Mid-Term Storage | -9.94 | 1 |  | 59.92 | 0.4542 | 45.4199 | 45.4199 | 14.5001 | 0 | 0 | 59.92 | 0 | 0 | 0 | 67.245 | 66.9799 | 68.1229 | 66.3786 | 67.8394 | 66.1106 | 2147.9136 | 0 | 14.5001 | 0 | 14.5001 | 0.8997 | 0 | 0 | 8.1647 | 8.1647
2025-01-16 01:00 | 1 | short_term | Short / Mid-Term Storage | -9.96 | 1 |  | 59.95 | 0.455 | 45.5042 | 45.5042 | 14.4458 | 0 | 0 | 59.95 | 0 | 0 | 0 | 66.9799 | 66.7158 | 67.8394 | 66.1106 | 67.5748 | 65.8348 | 2132.5746 | 0 | 14.4458 | 0 | 14.4458 | 0.8932 | 0 | 0 | 8.1647 | 8.1647
2025-01-16 02:00 | 1 | short_term | Short / Mid-Term Storage | -9.98 | 1 |  | 59.97 | 0.4558 | 45.5825 | 45.5825 | 14.3875 | 0 | 0 | 59.97 | 0 | 0 | 0 | 66.7158 | 66.4528 | 67.5748 | 65.8348 | 67.3147 | 65.5783 | 2117.3002 | 0 | 14.3875 | 0 | 14.3875 | 0.8868 | 0 | 0 | 8.1647 | 8.1647
2025-01-16 03:00 | 1 | short_term | Short / Mid-Term Storage | -9.99 | 1 |  | 59.99 | 0.4566 | 45.6625 | 45.6625 | 14.3275 | 0 | 0 | 59.99 | 0 | 0 | 0 | 66.4528 | 66.191 | 67.3147 | 65.5783 | 67.0505 | 65.3266 | 2102.0922 | 0 | 14.3275 | 0 | 14.3275 | 0.8805 | 0 | 0 | 8.1647 | 8.1647
2025-01-16 04:00 | 1 | short_term | Short / Mid-Term Storage | -10 | 1 |  | 60 | 0.4574 | 45.7438 | 45.7438 | 14.2562 | 0 | 0 | 60 | 0 | 0 | 0 | 66.191 | 65.9305 | 67.0505 | 65.3266 | 66.8017 | 65.0723 | 2086.9619 | 0 | 14.2562 | 0 | 14.2562 | 0.8741 | 0 | 0 | 8.1647 | 8.1647

## MonthlyAnnual
month | heating_load_kwh | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated | annualized_total_cost | solar_coverage_pct
2025-01 | 13687.6 | 55610.7632 | 12741.3475 | 737.3249 | 0 | 208.9276 | 59.6936 | 3130.3033 | 737.3249 | 306.0166 | 7.1632 | 2980.1122 | 2987.2754
annual | 13687.6 | 55610.7632 | 12741.3475 | 737.3249 | 0 | 208.9276 | 59.6936 | 3130.3033 | 737.3249 | 306.0166 | 7.1632 | 2980.1122 | 2987.2754 | 2987.2754 | 98.4736