## Step1_Collector_Study
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct | study_ratio_l_per_m2
seasonal | Long-Term / Seasonal Storage | 50 | 100 | 5808.3333 | 35 | 57.0568 | 35 | 2 | TRUE | 3 | 300 | 15000 | 39286.4249 | 2714.3212 | 31.7179 | 2746.0392 | 27963.3298 | 8730.9428 | 4031.5513 | 925.1059 | 660.7899 | 13423.284 | 13687.6 | 0 | 264.316 | 264.316 | 14449.0755 | 4783.3115 | 4692.3412 | 90.9703 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 114.286 | 228.572 | 13276.2237 | 35 | 78.1303 | 35 | 2 | TRUE | 3 | 300 | 34285.8 | 77382.257 | 5583.4029 | 0 | 5583.4029 | 62462.8111 | 12823.5585 | 864.0415 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 48477.8557 | 1161.397 | 864.0415 | 297.3554 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 178.571 | 357.142 | 20743.9978 | 35 | 79.9969 | 35 | 2 | TRUE | 3 | 300 | 53571.3 | 111576.3291 | 8257.3815 | 0 | 8257.3815 | 97465.4412 | 13687.6 | 0 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 83304.2783 | 473.5629 | 0 | 473.5629 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 242.857 | 485.714 | 28211.8882 | 35 | 79.9969 | 35 | 2 | TRUE | 3 | 300 | 72857.1 | 143573.6096 | 10821.5355 | 0 | 10821.5355 | 132553.2402 | 13687.6 | 0 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 118221.5935 | 644.0467 | 0 | 644.0467 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 307.143 | 614.286 | 35679.7785 | 35 | 79.9969 | 35 | 2 | TRUE | 3 | 300 | 92142.9 | 174062.9805 | 13310.294 | 0 | 13310.294 | 167641.0392 | 13687.6 | 0 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 153138.9086 | 814.5305 | 0 | 814.5305 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 371.429 | 742.858 | 43147.6688 | 35 | 79.9969 | 35 | 2 | TRUE | 3 | 300 | 111428.7 | 203416.0746 | 15742.2387 | 0 | 15742.2387 | 202728.8382 | 13687.6 | 0 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 188056.2238 | 985.0144 | 0 | 985.0144 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 435.714 | 871.428 | 50615.443 | 35 | 79.9969 | 35 | 2 | TRUE | 3 | 300 | 130714.2 | 231863.4789 | 18128.8839 | 0 | 18128.8839 | 237816.0913 | 13687.6 | 0 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 222972.9958 | 1155.4955 | 0 | 1155.4955 | 13687.6 | 100 | 0 | 2000
seasonal | Long-Term / Seasonal Storage | 500 | 1000 | 58083.3333 | 35 | 79.9969 | 35 | 2 | TRUE | 3 | 300 | 150000 | 259562.8353 | 20478.1418 | 0 | 20478.1418 | 272903.8903 | 13687.6 | 0 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 257890.311 | 1325.9793 | 0 | 1325.9793 | 13687.6 | 100 | 0 | 2000

## Step2_Tank_Study
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct
seasonal | Long-Term / Seasonal Storage | 50 | 10 | 580.8333 | 35 | 34.9799 | 35 | 1 | TRUE | 3 | 300 | 15000 | 5946.241 | 1047.3121 | 144.1854 | 1191.4974 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 116.0919 | 9598.2854 | 9644.7221 | 4042.8779 | 1201.5447 | 46.4367 | 18661.7779 | 529.0192 | 522.0303 | 7.2218 | 13687.6 | 70.4632 | 29.5368
seasonal | Long-Term / Seasonal Storage | 50 | 94.286 | 5476.4452 | 35 | 55.7511 | 35 | 2 | TRUE | 3 | 300 | 15000 | 37435.9814 | 2621.7991 | 38.9163 | 2660.7154 | 27981.964 | 8749.6855 | 3802.8559 | 1135.0587 | 810.7562 | 13363.2975 | 13687.6 | 0 | 324.3025 | 324.3025 | 14534.6341 | 4697.6444 | 4613.612 | 84.0324 | 13687.6 | 100 | 0
seasonal | Long-Term / Seasonal Storage | 50 | 178.571 | 10371.9989 | 35 | 66.7612 | 35 | 2 | TRUE | 3 | 300 | 15000 | 63201.5126 | 3910.0756 | 0 | 3910.0756 | 27709.9954 | 8496.2137 | 5191.3863 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 13831.1915 | 5382.5902 | 5191.3863 | 191.2039 | 13687.6 | 100 | 0
seasonal | Long-Term / Seasonal Storage | 50 | 262.857 | 15267.6108 | 35 | 70.8372 | 35 | 2 | TRUE | 3 | 300 | 15000 | 86778.5797 | 5088.929 | 0 | 5088.929 | 27583.8486 | 8382.6528 | 5304.9472 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 13594.7895 | 5606.4062 | 5304.9472 | 301.4591 | 13687.6 | 100 | 0
seasonal | Long-Term / Seasonal Storage | 50 | 347.143 | 20163.2226 | 35 | 72.96 | 35 | 2 | TRUE | 3 | 300 | 15000 | 109008.26 | 6200.413 | 0 | 6200.413 | 27517.2143 | 8323.0631 | 5364.5369 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 13417.4869 | 5776.6642 | 5364.5369 | 412.1274 | 13687.6 | 100 | 0
seasonal | Long-Term / Seasonal Storage | 50 | 431.429 | 25058.8344 | 35 | 74.2622 | 35 | 3 | TRUE | 3 | 300 | 15000 | 130277.1243 | 7263.8562 | 0 | 7263.8562 | 27475.9812 | 8286.0303 | 5401.5697 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 13265.4092 | 5924.5417 | 5401.5697 | 522.9721 | 13687.6 | 100 | 0
seasonal | Long-Term / Seasonal Storage | 50 | 515.714 | 29954.3882 | 35 | 75.1425 | 35 | 3 | TRUE | 3 | 300 | 15000 | 150805.7236 | 8290.2862 | 0 | 8290.2862 | 27447.9984 | 8260.9371 | 5426.6629 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 13126.4942 | 6060.5671 | 5426.6629 | 633.9042 | 13687.6 | 100 | 0
seasonal | Long-Term / Seasonal Storage | 50 | 600 | 34850 | 35 | 75.7775 | 35 | 3 | TRUE | 3 | 300 | 15000 | 170736.563 | 9286.8282 | 0 | 9286.8282 | 27427.7433 | 8242.8109 | 5444.7891 | 0 | 0 | 13687.6 | 13687.6 | 0 | 0 | 0 | 12995.2531 | 6189.6793 | 5444.7891 | 744.8902 | 13687.6 | 100 | 0

## Final_Selected_Summary
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct
seasonal | Long-Term / Seasonal Storage | 50 | 10 | 580.8333 | 35 | 34.9799 | 35 | 1 | TRUE | 3 | 300 | 15000 | 5946.241 | 1047.3121 | 144.1854 | 1191.4974 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 116.0919 | 9598.2854 | 9644.7221 | 4042.8779 | 1201.5447 | 46.4367 | 18661.7779 | 529.0192 | 522.0303 | 7.2218 | 13687.6 | 70.4632 | 29.5368

## Final_Selected_Hourly
timestamp | simulation_year_index | tank_type | tank_type_label | outside_temp_c | solar_rad_kwh_m2 | horizontal_solar_rad_kwh_m2 | heating_load_kwh | collector_efficiency | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_heating_total_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | tank_temp_start_c | tank_temp_end_c | tank_top_temp_start_c | tank_bottom_temp_start_c | tank_top_temp_end_c | tank_bottom_temp_end_c | tank_stored_energy_kwh | tank_charge_kwh | tank_discharge_direct_kwh | tank_discharge_hp_source_kwh | tank_discharge_total_kwh | tank_loss_kwh | solar_energy_curtailed_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated
2025-01-01 | 1 | seasonal | Long-Term / Seasonal Storage | -10 | 1 |  | 60 | 0.528 | 26.4 | 26.4 | 0 | 0 | 0 | 26.4 | 33.6 | 9.6 | 0 | 35 | 34.9997 | 35 | 35 | 34.9997 | 34.9997 | 58.0797 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.152 | 2.8693 | 4.0213
2025-01-01 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -10 | 1 |  | 60 | 0.528 | 26.4 | 26.4 | 0 | 0 | 0 | 26.4 | 33.6 | 9.6 | 0 | 34.9997 | 34.9994 | 34.9997 | 34.9997 | 34.9994 | 34.9994 | 58.0761 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.152 | 2.8693 | 4.0213
2025-01-01 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.99 | 1 |  | 59.99 | 0.528 | 26.4016 | 26.4016 | 0 | 0 | 0 | 26.4016 | 33.5884 | 9.5967 | 0 | 34.9994 | 34.9991 | 34.9994 | 34.9994 | 34.9991 | 34.9991 | 58.0724 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1516 | 2.8693 | 4.021
2025-01-01 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.98 | 1 |  | 59.97 | 0.5281 | 26.4032 | 26.4032 | 0 | 0 | 0 | 26.4032 | 33.5668 | 9.5905 | 0 | 34.9991 | 34.9987 | 34.9991 | 34.9991 | 34.9987 | 34.9987 | 58.0688 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1509 | 2.8693 | 4.0202
2025-01-01 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.96 | 1 |  | 59.95 | 0.5281 | 26.4064 | 26.4064 | 0 | 0 | 0 | 26.4064 | 33.5436 | 9.5839 | 0 | 34.9987 | 34.9984 | 34.9987 | 34.9987 | 34.9984 | 34.9984 | 58.0652 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1501 | 2.8693 | 4.0194
2025-01-01 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.94 | 1 |  | 59.92 | 0.5282 | 26.4096 | 26.4096 | 0 | 0 | 0 | 26.4096 | 33.5104 | 9.5744 | 0 | 34.9984 | 34.9981 | 34.9984 | 34.9984 | 34.9981 | 34.9981 | 58.0615 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1489 | 2.8693 | 4.0183
2025-01-01 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.92 | 1 |  | 59.88 | 0.5283 | 26.4128 | 26.4128 | 0 | 0 | 0 | 26.4128 | 33.4672 | 9.5621 | 0 | 34.9981 | 34.9978 | 34.9981 | 34.9981 | 34.9978 | 34.9978 | 58.0579 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1474 | 2.8693 | 4.0168
2025-01-01 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.89 | 1 |  | 59.84 | 0.5284 | 26.4176 | 26.4176 | 0 | 0 | 0 | 26.4176 | 33.4224 | 9.5493 | 0 | 34.9978 | 34.9975 | 34.9978 | 34.9978 | 34.9975 | 34.9975 | 58.0543 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1459 | 2.8693 | 4.0153
2025-01-01 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.86 | 1 |  | 59.79 | 0.5284 | 26.4224 | 26.4224 | 0 | 0 | 0 | 26.4224 | 33.3676 | 9.5336 | 0 | 34.9975 | 34.9972 | 34.9975 | 34.9975 | 34.9972 | 34.9972 | 58.0506 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.144 | 2.8693 | 4.0134
2025-01-01 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.82 | 1 |  | 59.73 | 0.5286 | 26.4288 | 26.4288 | 0 | 0 | 0 | 26.4288 | 33.3012 | 9.5146 | 0 | 34.9972 | 34.9969 | 34.9972 | 34.9972 | 34.9969 | 34.9969 | 58.047 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1418 | 2.8693 | 4.0111
2025-01-01 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.78 | 1 |  | 59.67 | 0.5287 | 26.4352 | 26.4352 | 0 | 0 | 0 | 26.4352 | 33.2348 | 9.4957 | 0 | 34.9969 | 34.9966 | 34.9969 | 34.9969 | 34.9966 | 34.9966 | 58.0434 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1395 | 2.8693 | 4.0088
2025-01-01 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.73 | 1 |  | 59.6 | 0.5289 | 26.4432 | 26.4432 | 0 | 0 | 0 | 26.4432 | 33.1568 | 9.4734 | 0 | 34.9966 | 34.9962 | 34.9966 | 34.9966 | 34.9962 | 34.9962 | 58.0398 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1368 | 2.8693 | 4.0062
2025-01-01 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.68 | 1 |  | 59.52 | 0.529 | 26.4512 | 26.4512 | 0 | 0 | 0 | 26.4512 | 33.0688 | 9.4482 | 0 | 34.9962 | 34.9959 | 34.9962 | 34.9962 | 34.9959 | 34.9959 | 58.0361 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1338 | 2.8693 | 4.0031
2025-01-01 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.63 | 1 |  | 59.44 | 0.5292 | 26.4592 | 26.4592 | 0 | 0 | 0 | 26.4592 | 32.9808 | 9.4231 | 0 | 34.9959 | 34.9956 | 34.9959 | 34.9959 | 34.9956 | 34.9956 | 58.0325 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1308 | 2.8693 | 4.0001
2025-01-01 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.57 | 1 |  | 59.35 | 0.5294 | 26.4688 | 26.4688 | 0 | 0 | 0 | 26.4688 | 32.8812 | 9.3946 | 0 | 34.9956 | 34.9953 | 34.9956 | 34.9956 | 34.9953 | 34.9953 | 58.0289 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1274 | 2.8693 | 3.9967
2025-01-01 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.5 | 1 |  | 59.25 | 0.5296 | 26.48 | 26.48 | 0 | 0 | 0 | 26.48 | 32.77 | 9.3629 | 0 | 34.9953 | 34.995 | 34.9953 | 34.9953 | 34.995 | 34.995 | 58.0252 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1235 | 2.8693 | 3.9929
2025-01-01 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.43 | 1 |  | 59.15 | 0.5298 | 26.4912 | 26.4912 | 0 | 0 | 0 | 26.4912 | 32.6588 | 9.3311 | 0 | 34.995 | 34.9947 | 34.995 | 34.995 | 34.9947 | 34.9947 | 58.0216 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1197 | 2.8693 | 3.9891
2025-01-01 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.36 | 1 |  | 59.04 | 0.53 | 26.5024 | 26.5024 | 0 | 0 | 0 | 26.5024 | 32.5376 | 9.2965 | 0 | 34.9947 | 34.9944 | 34.9947 | 34.9947 | 34.9944 | 34.9944 | 58.018 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1156 | 2.8693 | 3.9849
2025-01-01 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.29 | 1 |  | 58.93 | 0.5303 | 26.5136 | 26.5136 | 0 | 0 | 0 | 26.5136 | 32.4164 | 9.2618 | 0 | 34.9944 | 34.9941 | 34.9944 | 34.9944 | 34.9941 | 34.9941 | 58.0143 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1114 | 2.8693 | 3.9808
2025-01-01 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.2 | 1 |  | 58.81 | 0.5306 | 26.528 | 26.528 | 0 | 0 | 0 | 26.528 | 32.282 | 9.2234 | 0 | 34.9941 | 34.9937 | 34.9941 | 34.9941 | 34.9937 | 34.9937 | 58.0107 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1068 | 2.8693 | 3.9762
2025-01-01 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.12 | 1 |  | 58.68 | 0.5308 | 26.5408 | 26.5408 | 0 | 0 | 0 | 26.5408 | 32.1392 | 9.1826 | 0 | 34.9937 | 34.9934 | 34.9937 | 34.9937 | 34.9934 | 34.9934 | 58.0071 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1019 | 2.8693 | 3.9713
2025-01-01 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.03 | 1 |  | 58.55 | 0.5311 | 26.5552 | 26.5552 | 0 | 0 | 0 | 26.5552 | 31.9948 | 9.1414 | 0 | 34.9934 | 34.9931 | 34.9934 | 34.9934 | 34.9931 | 34.9931 | 58.0035 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.097 | 2.8693 | 3.9663
2025-01-01 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.94 | 1 |  | 58.41 | 0.5314 | 26.5696 | 26.5696 | 0 | 0 | 0 | 26.5696 | 31.8404 | 9.0973 | 0 | 34.9931 | 34.9928 | 34.9931 | 34.9931 | 34.9928 | 34.9928 | 57.9998 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0917 | 2.8693 | 3.961
2025-01-01 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.84 | 1 |  | 58.26 | 0.5317 | 26.5856 | 26.5856 | 0 | 0 | 0 | 26.5856 | 31.6744 | 9.0498 | 0 | 34.9928 | 34.9925 | 34.9928 | 34.9928 | 34.9925 | 34.9925 | 57.9962 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.086 | 2.8693 | 3.9553
2025-01-02 | 1 | seasonal | Long-Term / Seasonal Storage | -8.74 | 1 |  | 58.11 | 0.532 | 26.6016 | 26.6016 | 0 | 0 | 0 | 26.6016 | 31.5084 | 9.0024 | 0 | 34.9925 | 34.9922 | 34.9925 | 34.9925 | 34.9922 | 34.9922 | 57.9926 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0803 | 2.8693 | 3.9496
2025-01-02 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.63 | 1 |  | 57.95 | 0.5324 | 26.6192 | 26.6192 | 0 | 0 | 0 | 26.6192 | 31.3308 | 8.9517 | 0 | 34.9922 | 34.9919 | 34.9922 | 34.9922 | 34.9919 | 34.9919 | 57.989 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0742 | 2.8693 | 3.9435
2025-01-02 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.52 | 1 |  | 57.78 | 0.5327 | 26.6368 | 26.6368 | 0 | 0 | 0 | 26.6368 | 31.1432 | 8.8981 | 0 | 34.9919 | 34.9916 | 34.9919 | 34.9919 | 34.9916 | 34.9916 | 57.9853 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0678 | 2.8693 | 3.9371
2025-01-02 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.41 | 1 |  | 57.61 | 0.5331 | 26.6544 | 26.6544 | 0 | 0 | 0 | 26.6544 | 30.9556 | 8.8445 | 0 | 34.9916 | 34.9913 | 34.9916 | 34.9916 | 34.9913 | 34.9913 | 57.9817 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0613 | 2.8693 | 3.9307
2025-01-02 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.29 | 1 |  | 57.44 | 0.5335 | 26.6736 | 26.6736 | 0 | 0 | 0 | 26.6736 | 30.7664 | 8.7904 | 0 | 34.9913 | 34.9909 | 34.9913 | 34.9913 | 34.9909 | 34.9909 | 57.9781 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0548 | 2.8693 | 3.9242
2025-01-02 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.17 | 1 |  | 57.25 | 0.5339 | 26.6928 | 26.6928 | 0 | 0 | 0 | 26.6928 | 30.5572 | 8.7306 | 0 | 34.9909 | 34.9906 | 34.9909 | 34.9909 | 34.9906 | 34.9906 | 57.9744 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0477 | 2.8693 | 3.917
2025-01-02 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.04 | 1 |  | 57.07 | 0.5343 | 26.7136 | 26.7136 | 0 | 0 | 0 | 26.7136 | 30.3564 | 8.6733 | 0 | 34.9906 | 34.9903 | 34.9906 | 34.9906 | 34.9903 | 34.9903 | 57.9708 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0408 | 2.8693 | 3.9101
2025-01-02 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.91 | 1 |  | 56.87 | 0.5347 | 26.7344 | 26.7344 | 0 | 0 | 0 | 26.7344 | 30.1356 | 8.6102 | 0 | 34.9903 | 34.99 | 34.9903 | 34.9903 | 34.99 | 34.99 | 57.9672 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0332 | 2.8693 | 3.9026
2025-01-02 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.78 | 1 |  | 56.67 | 0.5351 | 26.7552 | 26.7552 | 0 | 0 | 0 | 26.7552 | 29.9148 | 8.5471 | 0 | 34.99 | 34.9897 | 34.99 | 34.99 | 34.9897 | 34.9897 | 57.9636 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0257 | 2.8693 | 3.895
2025-01-02 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.64 | 1 |  | 56.47 | 0.5356 | 26.7776 | 26.7776 | 0 | 0 | 0 | 26.7776 | 29.6924 | 8.4835 | 0 | 34.9897 | 34.9894 | 34.9897 | 34.9897 | 34.9894 | 34.9894 | 57.9599 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.018 | 2.8693 | 3.8874
2025-01-02 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.5 | 1 |  | 56.26 | 0.536 | 26.8 | 26.8 | 0 | 0 | 0 | 26.8 | 29.46 | 8.4171 | 0 | 34.9894 | 34.9891 | 34.9894 | 34.9894 | 34.9891 | 34.9891 | 57.9563 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0101 | 2.8693 | 3.8794
2025-01-02 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.36 | 1 |  | 56.04 | 0.5364 | 26.8224 | 26.8224 | 0 | 0 | 0 | 26.8224 | 29.2176 | 8.3479 | 0 | 34.9891 | 34.9888 | 34.9891 | 34.9891 | 34.9888 | 34.9888 | 57.9527 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0017 | 2.8693 | 3.8711
2025-01-02 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.21 | 1 |  | 55.82 | 0.5369 | 26.8464 | 26.8464 | 0 | 0 | 0 | 26.8464 | 28.9736 | 8.2782 | 0 | 34.9888 | 34.9884 | 34.9888 | 34.9888 | 34.9884 | 34.9884 | 57.9491 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9934 | 2.8693 | 3.8627
2025-01-02 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.06 | 1 |  | 55.59 | 0.5374 | 26.8704 | 26.8704 | 0 | 0 | 0 | 26.8704 | 28.7196 | 8.2056 | 0 | 34.9884 | 34.9881 | 34.9884 | 34.9884 | 34.9881 | 34.9881 | 57.9454 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9847 | 2.8693 | 3.854
2025-01-02 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.9 | 1 |  | 55.36 | 0.5379 | 26.896 | 26.896 | 0 | 0 | 0 | 26.896 | 28.464 | 8.1326 | 0 | 34.9881 | 34.9878 | 34.9881 | 34.9881 | 34.9878 | 34.9878 | 57.9418 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9759 | 2.8693 | 3.8453
2025-01-02 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.74 | 1 |  | 55.12 | 0.5384 | 26.9216 | 26.9216 | 0 | 0 | 0 | 26.9216 | 28.1984 | 8.0567 | 0 | 34.9878 | 34.9875 | 34.9878 | 34.9878 | 34.9875 | 34.9875 | 57.9382 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9668 | 2.8693 | 3.8362
2025-01-02 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.58 | 1 |  | 54.87 | 0.5389 | 26.9472 | 26.9472 | 0 | 0 | 0 | 26.9472 | 27.9228 | 7.9779 | 0 | 34.9875 | 34.9872 | 34.9875 | 34.9875 | 34.9872 | 34.9872 | 57.9346 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9574 | 2.8693 | 3.8267
2025-01-02 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.42 | 1 |  | 54.62 | 0.5395 | 26.9728 | 26.9728 | 0 | 0 | 0 | 26.9728 | 27.6472 | 7.8992 | 0 | 34.9872 | 34.9869 | 34.9872 | 34.9872 | 34.9869 | 34.9869 | 57.931 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9479 | 2.8693 | 3.8173
2025-01-02 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.25 | 1 |  | 54.37 | 0.54 | 27 | 27 | 0 | 0 | 0 | 27 | 27.37 | 7.82 | 0 | 34.9869 | 34.9866 | 34.9869 | 34.9869 | 34.9866 | 34.9866 | 57.9273 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9384 | 2.8693 | 3.8077
2025-01-02 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.07 | 1 |  | 54.11 | 0.5406 | 27.0288 | 27.0288 | 0 | 0 | 0 | 27.0288 | 27.0812 | 7.7375 | 0 | 34.9866 | 34.9863 | 34.9866 | 34.9866 | 34.9863 | 34.9863 | 57.9237 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9285 | 2.8693 | 3.7978
2025-01-02 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.9 | 1 |  | 53.85 | 0.5411 | 27.056 | 27.056 | 0 | 0 | 0 | 27.056 | 26.794 | 7.6554 | 0 | 34.9863 | 34.9859 | 34.9863 | 34.9863 | 34.9859 | 34.9859 | 57.9201 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9187 | 2.8693 | 3.788
2025-01-02 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.72 | 1 |  | 53.58 | 0.5417 | 27.0848 | 27.0848 | 0 | 0 | 0 | 27.0848 | 26.4952 | 7.5701 | 0 | 34.9859 | 34.9856 | 34.9859 | 34.9859 | 34.9856 | 34.9856 | 57.9165 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9084 | 2.8693 | 3.7778
2025-01-02 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.54 | 1 |  | 53.31 | 0.5423 | 27.1136 | 27.1136 | 0 | 0 | 0 | 27.1136 | 26.1964 | 7.4847 | 0 | 34.9856 | 34.9853 | 34.9856 | 34.9856 | 34.9853 | 34.9853 | 57.9128 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8982 | 2.8693 | 3.7675
2025-01-02 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.35 | 1 |  | 53.03 | 0.5429 | 27.144 | 27.144 | 0 | 0 | 0 | 27.144 | 25.886 | 7.396 | 0 | 34.9853 | 34.985 | 34.9853 | 34.9853 | 34.985 | 34.985 | 57.9092 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8875 | 2.8693 | 3.7569
2025-01-03 | 1 | seasonal | Long-Term / Seasonal Storage | -5.16 | 1 |  | 52.75 | 0.5435 | 27.1744 | 27.1744 | 0 | 0 | 0 | 27.1744 | 25.5756 | 7.3073 | 0 | 34.985 | 34.9847 | 34.985 | 34.985 | 34.9847 | 34.9847 | 57.9056 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8769 | 2.8693 | 3.7462
2025-01-03 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.97 | 1 |  | 52.46 | 0.5441 | 27.2048 | 27.2048 | 0 | 0 | 0 | 27.2048 | 25.2552 | 7.2158 | 0 | 34.9847 | 34.9844 | 34.9847 | 34.9847 | 34.9844 | 34.9844 | 57.902 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8659 | 2.8693 | 3.7352
2025-01-03 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.78 | 1 |  | 52.17 | 0.5447 | 27.2352 | 27.2352 | 0 | 0 | 0 | 27.2352 | 24.9348 | 7.1242 | 0 | 34.9844 | 34.9841 | 34.9844 | 34.9844 | 34.9841 | 34.9841 | 57.8983 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8549 | 2.8693 | 3.7243
2025-01-03 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.58 | 1 |  | 51.87 | 0.5453 | 27.2672 | 27.2672 | 0 | 0 | 0 | 27.2672 | 24.6028 | 7.0294 | 0 | 34.9841 | 34.9838 | 34.9841 | 34.9841 | 34.9838 | 34.9838 | 57.8947 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8435 | 2.8693 | 3.7129
2025-01-03 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.38 | 1 |  | 51.57 | 0.546 | 27.2992 | 27.2992 | 0 | 0 | 0 | 27.2992 | 24.2708 | 6.9345 | 0 | 34.9838 | 34.9835 | 34.9838 | 34.9838 | 34.9835 | 34.9835 | 57.8911 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8321 | 2.8693 | 3.7015
2025-01-03 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.18 | 1 |  | 51.27 | 0.5466 | 27.3312 | 27.3312 | 0 | 0 | 0 | 27.3312 | 23.9388 | 6.8397 | 0 | 34.9835 | 34.9831 | 34.9835 | 34.9835 | 34.9831 | 34.9831 | 57.8875 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8208 | 2.8693 | 3.6901
2025-01-03 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.97 | 1 |  | 50.96 | 0.5473 | 27.3648 | 27.3648 | 0 | 0 | 0 | 27.3648 | 23.5952 | 6.7415 | 0 | 34.9831 | 34.9828 | 34.9831 | 34.9831 | 34.9828 | 34.9828 | 57.8839 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.809 | 2.8693 | 3.6783
2025-01-03 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.76 | 1 |  | 50.65 | 0.548 | 27.3984 | 27.3984 | 0 | 0 | 0 | 27.3984 | 23.2516 | 6.6433 | 0 | 34.9828 | 34.9825 | 34.9828 | 34.9828 | 34.9825 | 34.9825 | 57.8802 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7972 | 2.8693 | 3.6665
2025-01-03 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.55 | 1 |  | 50.33 | 0.5486 | 27.432 | 27.432 | 0 | 0 | 0 | 27.432 | 22.898 | 6.5423 | 0 | 34.9825 | 34.9822 | 34.9825 | 34.9825 | 34.9822 | 34.9822 | 57.8766 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7851 | 2.8693 | 3.6544
2025-01-03 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.34 | 1 |  | 50.01 | 0.5493 | 27.4656 | 27.4656 | 0 | 0 | 0 | 27.4656 | 22.5444 | 6.4413 | 0 | 34.9822 | 34.9819 | 34.9822 | 34.9822 | 34.9819 | 34.9819 | 57.873 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.773 | 2.8693 | 3.6423
2025-01-03 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.12 | 1 |  | 49.69 | 0.55 | 27.5008 | 27.5008 | 0 | 0 | 0 | 27.5008 | 22.1892 | 6.3398 | 0 | 34.9819 | 34.9816 | 34.9819 | 34.9819 | 34.9816 | 34.9816 | 57.8694 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7608 | 2.8693 | 3.6301
2025-01-03 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.91 | 1 |  | 49.36 | 0.5507 | 27.5344 | 27.5344 | 0 | 0 | 0 | 27.5344 | 21.8256 | 6.2359 | 0 | 34.9816 | 34.9813 | 34.9816 | 34.9816 | 34.9813 | 34.9813 | 57.8658 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7483 | 2.8693 | 3.6177
2025-01-03 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.69 | 1 |  | 49.03 | 0.5514 | 27.5696 | 27.5696 | 0 | 0 | 0 | 27.5696 | 21.4604 | 6.1315 | 0 | 34.9813 | 34.981 | 34.9813 | 34.9813 | 34.981 | 34.981 | 57.8621 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7358 | 2.8693 | 3.6051
2025-01-03 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.46 | 1 |  | 48.69 | 0.5521 | 27.6064 | 27.6064 | 0 | 0 | 0 | 27.6064 | 21.0836 | 6.0239 | 0 | 34.981 | 34.9806 | 34.981 | 34.981 | 34.9806 | 34.9806 | 57.8585 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7229 | 2.8693 | 3.5922
2025-01-03 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.24 | 1 |  | 48.36 | 0.5528 | 27.6416 | 27.6416 | 0 | 0 | 0 | 27.6416 | 20.7184 | 5.9195 | 0 | 34.9806 | 34.9803 | 34.9806 | 34.9806 | 34.9803 | 34.9803 | 57.8549 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7103 | 2.8693 | 3.5797
2025-01-03 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.01 | 1 |  | 48.02 | 0.5536 | 27.6784 | 27.6784 | 0 | 0 | 0 | 27.6784 | 20.3416 | 5.8119 | 0 | 34.9803 | 34.98 | 34.9803 | 34.9803 | 34.98 | 34.98 | 57.8513 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6974 | 2.8693 | 3.5668
2025-01-03 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.78 | 1 |  | 47.67 | 0.5543 | 27.7152 | 27.7152 | 0 | 0 | 0 | 27.7152 | 19.9548 | 5.7014 | 0 | 34.98 | 34.9797 | 34.98 | 34.98 | 34.9797 | 34.9797 | 57.8477 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6842 | 2.8693 | 3.5535
2025-01-03 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.55 | 1 |  | 47.32 | 0.555 | 27.752 | 27.752 | 0 | 0 | 0 | 27.752 | 19.568 | 5.5909 | 0 | 34.9797 | 34.9794 | 34.9797 | 34.9797 | 34.9794 | 34.9794 | 57.8441 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6709 | 2.8693 | 3.5403
2025-01-03 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.32 | 1 |  | 46.97 | 0.5558 | 27.7888 | 27.7888 | 0 | 0 | 0 | 27.7888 | 19.1812 | 5.4803 | 0 | 34.9794 | 34.9791 | 34.9794 | 34.9794 | 34.9791 | 34.9791 | 57.8404 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6576 | 2.8693 | 3.527
2025-01-03 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.08 | 1 |  | 46.62 | 0.5565 | 27.8272 | 27.8272 | 0 | 0 | 0 | 27.8272 | 18.7928 | 5.3694 | 0 | 34.9791 | 34.9788 | 34.9791 | 34.9791 | 34.9788 | 34.9788 | 57.8368 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6443 | 2.8693 | 3.5137
2025-01-03 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.84 | 1 |  | 46.27 | 0.5573 | 27.8656 | 27.8656 | 0 | 0 | 0 | 27.8656 | 18.4044 | 5.2584 | 0 | 34.9788 | 34.9785 | 34.9788 | 34.9788 | 34.9785 | 34.9785 | 57.8332 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.631 | 2.8693 | 3.5004
2025-01-03 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.61 | 1 |  | 45.91 | 0.558 | 27.9024 | 27.9024 | 0 | 0 | 0 | 27.9024 | 18.0076 | 5.145 | 0 | 34.9785 | 34.9782 | 34.9785 | 34.9785 | 34.9782 | 34.9782 | 57.8296 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6174 | 2.8693 | 3.4868
2025-01-03 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.37 | 1 |  | 45.55 | 0.5588 | 27.9408 | 27.9408 | 0 | 0 | 0 | 27.9408 | 17.6092 | 5.0312 | 0 | 34.9782 | 34.9778 | 34.9782 | 34.9782 | 34.9778 | 34.9778 | 57.826 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6037 | 2.8693 | 3.4731
2025-01-03 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.12 | 1 |  | 45.19 | 0.5596 | 27.9808 | 27.9808 | 0 | 0 | 0 | 27.9808 | 17.2092 | 4.9169 | 0 | 34.9778 | 34.9775 | 34.9778 | 34.9778 | 34.9775 | 34.9775 | 57.8224 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.59 | 2.8693 | 3.4594
2025-01-04 | 1 | seasonal | Long-Term / Seasonal Storage | 0.12 | 1 |  | 44.82 | 0.5604 | 28.0192 | 28.0192 | 0 | 0 | 0 | 28.0192 | 16.8008 | 4.8002 | 0 | 34.9775 | 34.9772 | 34.9775 | 34.9775 | 34.9772 | 34.9772 | 57.8187 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.576 | 2.8693 | 3.4454
2025-01-04 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.36 | 1 |  | 44.45 | 0.5612 | 28.0576 | 28.0576 | 0 | 0 | 0 | 28.0576 | 16.3924 | 4.6835 | 0 | 34.9772 | 34.9769 | 34.9772 | 34.9772 | 34.9769 | 34.9769 | 57.8151 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.562 | 2.8693 | 3.4314
2025-01-04 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.61 | 1 |  | 44.08 | 0.562 | 28.0976 | 28.0976 | 0 | 0 | 0 | 28.0976 | 15.9824 | 4.5664 | 0 | 34.9769 | 34.9766 | 34.9769 | 34.9769 | 34.9766 | 34.9766 | 57.8115 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.548 | 2.8693 | 3.4173
2025-01-04 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.86 | 1 |  | 43.71 | 0.5628 | 28.1376 | 28.1376 | 0 | 0 | 0 | 28.1376 | 15.5724 | 4.4493 | 0 | 34.9766 | 34.9763 | 34.9766 | 34.9766 | 34.9763 | 34.9763 | 57.8079 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.5339 | 2.8693 | 3.4033
2025-01-04 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.11 | 1 |  | 43.34 | 0.5636 | 28.1776 | 28.1776 | 0 | 0 | 0 | 28.1776 | 15.1624 | 4.3321 | 0 | 34.9763 | 34.976 | 34.9763 | 34.9763 | 34.976 | 34.976 | 57.8043 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.5199 | 2.8693 | 3.3892
2025-01-04 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.36 | 1 |  | 42.96 | 0.5644 | 28.2176 | 28.2176 | 0 | 0 | 0 | 28.2176 | 14.7424 | 4.2121 | 0 | 34.976 | 34.9757 | 34.976 | 34.976 | 34.9757 | 34.9757 | 57.8007 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.5055 | 2.8693 | 3.3748
2025-01-04 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.61 | 1 |  | 42.59 | 0.5652 | 28.2576 | 28.2576 | 0 | 0 | 0 | 28.2576 | 14.3324 | 4.095 | 0 | 34.9757 | 34.9754 | 34.9757 | 34.9757 | 34.9754 | 34.9754 | 57.797 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4914 | 2.8693 | 3.3607
2025-01-04 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.86 | 1 |  | 42.21 | 0.566 | 28.2976 | 28.2976 | 0 | 0 | 0 | 28.2976 | 13.9124 | 3.975 | 0 | 34.9754 | 34.975 | 34.9754 | 34.9754 | 34.975 | 34.975 | 57.7934 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.477 | 2.8693 | 3.3463
2025-01-04 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.11 | 1 |  | 41.83 | 0.5668 | 28.3376 | 28.3376 | 0 | 0 | 0 | 28.3376 | 13.4924 | 3.855 | 0 | 34.975 | 34.9747 | 34.975 | 34.975 | 34.9747 | 34.9747 | 57.7898 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4626 | 2.8693 | 3.3319
2025-01-04 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.37 | 1 |  | 41.45 | 0.5676 | 28.3792 | 28.3792 | 0 | 0 | 0 | 28.3792 | 13.0708 | 3.7345 | 0 | 34.9747 | 34.9744 | 34.9747 | 34.9747 | 34.9744 | 34.9744 | 57.7862 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4481 | 2.8693 | 3.3175
2025-01-04 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.62 | 1 |  | 41.07 | 0.5684 | 28.4192 | 28.4192 | 0 | 0 | 0 | 28.4192 | 12.6508 | 3.6145 | 0 | 34.9744 | 34.9741 | 34.9744 | 34.9744 | 34.9741 | 34.9741 | 57.7826 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4337 | 2.8693 | 3.3031
2025-01-04 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.88 | 1 |  | 40.68 | 0.5692 | 28.4608 | 28.4608 | 0 | 0 | 0 | 28.4608 | 12.2192 | 3.4912 | 0 | 34.9741 | 34.9738 | 34.9741 | 34.9741 | 34.9738 | 34.9738 | 57.779 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4189 | 2.8693 | 3.2883
2025-01-04 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.13 | 1 |  | 40.3 | 0.57 | 28.5008 | 28.5008 | 0 | 0 | 0 | 28.5008 | 11.7992 | 3.3712 | 0 | 34.9738 | 34.9735 | 34.9738 | 34.9738 | 34.9735 | 34.9735 | 57.7754 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4045 | 2.8693 | 3.2739
2025-01-04 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.39 | 1 |  | 39.92 | 0.5708 | 28.5424 | 28.5424 | 0 | 0 | 0 | 28.5424 | 11.3776 | 3.2507 | 0 | 34.9735 | 34.9732 | 34.9735 | 34.9735 | 34.9732 | 34.9732 | 57.7717 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3901 | 2.8693 | 3.2594
2025-01-04 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.65 | 1 |  | 39.53 | 0.5717 | 28.584 | 28.584 | 0 | 0 | 0 | 28.584 | 10.946 | 3.1274 | 0 | 34.9732 | 34.9729 | 34.9732 | 34.9732 | 34.9729 | 34.9729 | 57.7681 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3753 | 2.8693 | 3.2446
2025-01-04 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.9 | 1 |  | 39.14 | 0.5725 | 28.624 | 28.624 | 0 | 0 | 0 | 28.624 | 10.516 | 3.0046 | 0 | 34.9729 | 34.9726 | 34.9729 | 34.9729 | 34.9726 | 34.9726 | 57.7645 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3605 | 2.8693 | 3.2299
2025-01-04 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.16 | 1 |  | 38.76 | 0.5733 | 28.6656 | 28.6656 | 0 | 0 | 0 | 28.6656 | 10.0944 | 2.8841 | 0 | 34.9726 | 34.9722 | 34.9726 | 34.9726 | 34.9722 | 34.9722 | 57.7609 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3461 | 2.8693 | 3.2154
2025-01-04 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.42 | 1 |  | 38.37 | 0.5741 | 28.7072 | 28.7072 | 0 | 0 | 0 | 28.7072 | 9.6628 | 2.7608 | 0 | 34.9722 | 34.9719 | 34.9722 | 34.9722 | 34.9719 | 34.9719 | 57.7573 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3313 | 2.8693 | 3.2006
2025-01-04 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.68 | 1 |  | 37.98 | 0.575 | 28.7488 | 28.7488 | 0 | 0 | 0 | 28.7488 | 9.2312 | 2.6375 | 0 | 34.9719 | 34.9716 | 34.9719 | 34.9719 | 34.9716 | 34.9716 | 57.7537 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3165 | 2.8693 | 3.1858
2025-01-04 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.94 | 1 |  | 37.6 | 0.5758 | 28.7904 | 28.7904 | 0 | 0 | 0 | 28.7904 | 8.8096 | 2.517 | 0 | 34.9716 | 34.9713 | 34.9716 | 34.9716 | 34.9713 | 34.9713 | 57.7501 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.302 | 2.8693 | 3.1714
2025-01-04 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.19 | 1.058 |  | 37.21 | 0.5845 | 30.9184 | 30.9184 | 0 | 0 | 0 | 30.9184 | 6.2916 | 1.7976 | 0 | 34.9713 | 34.971 | 34.9713 | 34.9713 | 34.971 | 34.971 | 57.7465 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.2157 | 2.8693 | 3.0851
2025-01-04 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.45 | 1.136 |  | 36.82 | 0.5945 | 33.768 | 33.768 | 0 | 0 | 0 | 33.768 | 3.052 | 0.872 | 0 | 34.971 | 34.9707 | 34.971 | 34.971 | 34.9707 | 34.9707 | 57.7428 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.1046 | 2.8693 | 2.974
2025-01-04 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.71 | 1.213 |  | 36.44 | 0.6032 | 36.5816 | 36.44 | 0 | 0 | 0 | 36.44 | 0 | 0 | 0 | 34.9707 | 34.9826 | 34.9707 | 34.9707 | 35.1166 | 34.9704 | 57.8808 | 0.1416 | 0 | 0 | 0 | 0.0036 | 0 | 0 | 2.8693 | 2.8693
2025-01-04 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.97 | 1.29 |  | 36.05 | 0.6108 | 39.3952 | 36.05 | 0 | 0 | 0 | 36.05 | 0 | 0 | 0 | 34.9826 | 35.2702 | 35.1166 | 34.9704 | 38.5717 | 34.9701 | 61.2222 | 3.3452 | 0 | 0 | 0 | 0.0038 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 | 1 | seasonal | Long-Term / Seasonal Storage | 6.23 | 1.368 |  | 35.66 | 0.6176 | 42.2448 | 35.66 | 0 | 0 | 0 | 35.66 | 0 | 0 | 0 | 35.2702 | 35.8367 | 38.5717 | 34.9701 | 45.3728 | 34.9698 | 67.8027 | 6.5848 | 0 | 0 | 0 | 0.0042 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.48 | 1.445 |  | 35.28 | 0.6228 | 44.9971 | 35.28 | 0 | 0 | 0 | 35.28 | 0 | 0 | 0 | 35.8367 | 36.6727 | 45.3728 | 34.9698 | 55.3712 | 34.9694 | 77.515 | 9.7171 | 0 | 0 | 0 | 0.0048 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.74 | 1.522 |  | 34.89 | 0.6072 | 46.211 | 34.89 | 0 | 0 | 0 | 34.89 | 0 | 0 | 0 | 36.6727 | 37.6468 | 55.3712 | 34.9694 | 65.369 | 34.9691 | 88.8305 | 11.321 | 0 | 0 | 0 | 0.0056 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7 | 1.599 |  | 34.51 | 0.5932 | 47.425 | 34.51 | 0 | 0 | 0 | 34.51 | 0 | 0 | 0 | 37.6468 | 38.758 | 65.369 | 34.9691 | 75.3662 | 34.9688 | 101.7391 | 12.915 | 0 | 0 | 0 | 0.0064 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.25 | 1.675 |  | 34.12 | 0.5803 | 48.6014 | 34.12 | 0 | 0 | 0 | 34.12 | 0 | 0 | 0 | 38.758 | 40.004 | 75.3662 | 34.9688 | 79.9969 | 34.9685 | 116.2132 | 14.4814 | 0 | 0 | 0 | 0.0073 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.51 | 1.752 |  | 33.74 | 0.5785 | 50.6741 | 33.74 | 0 | 0 | 0 | 33.74 | 0 | 0 | 0 | 40.004 | 41.461 | 79.9969 | 34.9685 | 79.9969 | 34.9682 | 133.139 | 16.9341 | 0 | 0 | 0 | 0.0083 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.76 | 1.828 |  | 33.36 | 0.5848 | 53.4501 | 33.36 | 0 | 0 | 0 | 33.36 | 0 | 0 | 0 | 41.461 | 43.1896 | 79.9969 | 34.9682 | 79.9969 | 34.9679 | 153.2195 | 20.0901 | 0 | 0 | 0 | 0.0096 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.01 | 1.904 |  | 32.98 | 0.5906 | 56.2261 | 32.98 | 0 | 0 | 0 | 32.98 | 0 | 0 | 0 | 43.1896 | 45.1898 | 79.9969 | 34.9679 | 79.9969 | 34.9676 | 176.4546 | 23.2461 | 0 | 0 | 0 | 0.011 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.27 | 1.98 |  | 32.6 | 0.596 | 59.0037 | 32.6 | 0 | 0 | 0 | 32.6 | 0 | 0 | 0 | 45.1898 | 47.4616 | 79.9969 | 34.9676 | 79.9969 | 34.9673 | 202.8456 | 26.4037 | 0 | 0 | 0 | 0.0127 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.52 | 2.055 |  | 32.22 | 0.6009 | 61.7437 | 32.22 | 0 | 0 | 0 | 32.22 | 0 | 0 | 0 | 47.4616 | 50.0018 | 79.9969 | 34.9673 | 79.9969 | 34.967 | 232.3548 | 29.5237 | 0 | 0 | 0 | 0.0145 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.77 | 2.13 |  | 31.85 | 0.6055 | 64.4837 | 31.85 | 0 | 0 | 0 | 31.85 | 0 | 0 | 0 | 50.0018 | 52.8096 | 79.9969 | 34.967 | 79.9969 | 34.9666 | 264.9719 | 32.6337 | 0 | 0 | 0 | 0.0166 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.02 | 2.205 |  | 31.47 | 0.6097 | 67.2237 | 31.47 | 0 | 0 | 0 | 31.47 | 0 | 0 | 0 | 52.8096 | 55.8858 | 79.9969 | 34.9666 | 79.9969 | 34.9663 | 300.7068 | 35.7537 | 0 | 0 | 0 | 0.0188 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.27 | 2.28 |  | 31.1 | 0.6137 | 69.9637 | 31.1 | 0 | 0 | 0 | 31.1 | 0 | 0 | 0 | 55.8858 | 59.2295 | 79.9969 | 34.9663 | 79.9969 | 34.966 | 339.5492 | 38.8637 | 0 | 0 | 0 | 0.0212 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.51 | 2.354 |  | 30.73 | 0.6174 | 72.6661 | 30.73 | 0 | 0 | 0 | 30.73 | 0 | 0 | 0 | 59.2295 | 62.8374 | 79.9969 | 34.966 | 79.9969 | 34.9657 | 381.4615 | 41.9361 | 0 | 0 | 0 | 0.0239 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.76 | 2.427 |  | 30.36 | 0.6208 | 75.3341 | 30.36 | 0 | 0 | 0 | 30.36 | 0 | 0 | 0 | 62.8374 | 66.7066 | 79.9969 | 34.9657 | 79.9969 | 34.9654 | 426.4089 | 44.9741 | 0 | 0 | 0 | 0.0267 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10 | 2.501 |  | 30 | 0.624 | 78.0365 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 66.7066 | 70.8392 | 79.9969 | 34.9654 | 79.9969 | 34.9651 | 474.4157 | 48.0365 | 0 | 0 | 0 | 0.0297 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.24 | 2.573 |  | 29.63 | 0.627 | 80.6669 | 29.63 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 70.8392 | 75.2298 | 79.9969 | 34.9651 | 79.9969 | 34.9648 | 525.4198 | 51.0369 | 0 | 0 | 0 | 0.0329 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.49 | 2.646 |  | 29.27 | 0.6299 | 83.3349 | 29.27 | 0 | 0 | 0 | 29.27 | 0 | 0 | 0 | 75.2298 | 79.8808 | 79.9969 | 34.9648 | 79.9969 | 78.6038 | 579.4484 | 54.0649 | 0 | 0 | 0 | 0.0362 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.73 | 2.718 |  | 28.91 | 0.6326 | 85.9653 | 28.91 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 79.8808 | 79.9969 | 79.9969 | 78.6038 | 79.9969 | 79.9969 | 580.797 | 1.3849 | 0 | 0 | 0 | 0.0363 | 55.6704 | 0 | 2.8693 | 2.8693
2025-01-05 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.96 | 2.789 |  | 28.56 | 0.6351 | 88.5581 | 28.56 | 0 | 0 | 0 | 28.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 59.9618 | 0 | 2.8693 | 2.8693
2025-01-05 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.2 | 2.86 |  | 28.2 | 0.6374 | 91.1525 | 28.2 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 62.9162 | 0 | 2.8693 | 2.8693
2025-01-05 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.43 | 2.93 |  | 27.85 | 0.6397 | 93.7093 | 27.85 | 0 | 0 | 0 | 27.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 65.823 | 0 | 2.8693 | 2.8693
2025-01-05 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.67 | 3 |  | 27.5 | 0.6418 | 96.2677 | 27.5 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 68.7314 | 0 | 2.8693 | 2.8693
2025-01-05 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.9 | 3.069 |  | 27.16 | 0.6438 | 98.7885 | 27.16 | 0 | 0 | 0 | 27.16 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 71.5922 | 0 | 2.8693 | 2.8693
2025-01-06 | 1 | seasonal | Long-Term / Seasonal Storage | 12.12 | 3.137 |  | 26.81 | 0.6457 | 101.2717 | 26.81 | 0 | 0 | 0 | 26.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 74.4254 | 0 | 2.8693 | 2.8693
2025-01-06 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.35 | 3.205 |  | 26.47 | 0.6475 | 103.7565 | 26.47 | 0 | 0 | 0 | 26.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 77.2502 | 0 | 2.8693 | 2.8693
2025-01-06 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.57 | 3.272 |  | 26.14 | 0.6492 | 106.2037 | 26.14 | 0 | 0 | 0 | 26.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 80.0274 | 0 | 2.8693 | 2.8693
2025-01-06 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.8 | 3.339 |  | 25.81 | 0.6508 | 108.6525 | 25.81 | 0 | 0 | 0 | 25.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 82.8062 | 0 | 2.8693 | 2.8693
2025-01-06 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.02 | 3.405 |  | 25.48 | 0.6524 | 111.0637 | 25.48 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 85.5474 | 0 | 2.8693 | 2.8693
2025-01-06 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.23 | 3.47 |  | 25.15 | 0.6538 | 113.4373 | 25.15 | 0 | 0 | 0 | 25.15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 88.251 | 0 | 2.8693 | 2.8693
2025-01-06 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.45 | 3.534 |  | 24.83 | 0.6552 | 115.7765 | 24.83 | 0 | 0 | 0 | 24.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 90.9102 | 0 | 2.8693 | 2.8693
2025-01-06 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.66 | 3.598 |  | 24.51 | 0.6566 | 118.1141 | 24.51 | 0 | 0 | 0 | 24.51 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 93.5678 | 0 | 2.8693 | 2.8693
2025-01-06 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.87 | 3.661 |  | 24.2 | 0.6578 | 120.4157 | 24.2 | 0 | 0 | 0 | 24.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 96.1794 | 0 | 2.8693 | 2.8693
2025-01-06 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.08 | 3.723 |  | 23.89 | 0.659 | 122.6813 | 23.89 | 0 | 0 | 0 | 23.89 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 98.755 | 0 | 2.8693 | 2.8693
2025-01-06 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.28 | 3.784 |  | 23.58 | 0.6602 | 124.9093 | 23.58 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 101.293 | 0 | 2.8693 | 2.8693
2025-01-06 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.48 | 3.844 |  | 23.28 | 0.6613 | 127.1013 | 23.28 | 0 | 0 | 0 | 23.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 103.785 | 0 | 2.8693 | 2.8693
2025-01-06 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.68 | 3.904 |  | 22.98 | 0.6624 | 129.2933 | 22.98 | 0 | 0 | 0 | 22.98 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 106.277 | 0 | 2.8693 | 2.8693
2025-01-06 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.88 | 3.963 |  | 22.69 | 0.6634 | 131.4493 | 22.69 | 0 | 0 | 0 | 22.69 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 108.723 | 0 | 2.8693 | 2.8693
2025-01-06 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.07 | 4.021 |  | 22.4 | 0.6644 | 133.5677 | 22.4 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 111.1314 | 0 | 2.8693 | 2.8693
2025-01-06 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.26 | 4.078 |  | 22.11 | 0.6653 | 135.6501 | 22.11 | 0 | 0 | 0 | 22.11 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 113.5038 | 0 | 2.8693 | 2.8693
2025-01-06 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.45 | 4.134 |  | 21.83 | 0.6662 | 137.6965 | 21.83 | 0 | 0 | 0 | 21.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 115.8302 | 0 | 2.8693 | 2.8693
2025-01-06 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.63 | 4.189 |  | 21.56 | 0.667 | 139.7053 | 21.56 | 0 | 0 | 0 | 21.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 118.109 | 0 | 2.8693 | 2.8693
2025-01-06 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.81 | 4.243 |  | 21.28 | 0.6678 | 141.6781 | 21.28 | 0 | 0 | 0 | 21.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 120.3618 | 0 | 2.8693 | 2.8693
2025-01-06 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.99 | 4.296 |  | 21.02 | 0.6686 | 143.6149 | 21.02 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 122.5586 | 0 | 2.8693 | 2.8693
2025-01-06 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.16 | 4.348 |  | 20.76 | 0.6693 | 145.5141 | 20.76 | 0 | 0 | 0 | 20.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 124.7178 | 0 | 2.8693 | 2.8693
2025-01-06 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.33 | 4.4 |  | 20.5 | 0.6701 | 147.4133 | 20.5 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 126.877 | 0 | 2.8693 | 2.8693
2025-01-06 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.5 | 4.45 |  | 20.25 | 0.6707 | 149.2405 | 20.25 | 0 | 0 | 0 | 20.25 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 128.9542 | 0 | 2.8693 | 2.8693
2025-01-06 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.66 | 4.499 |  | 20 | 0.6714 | 151.0301 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 130.9938 | 0 | 2.8693 | 2.8693
2025-01-07 | 1 | seasonal | Long-Term / Seasonal Storage | 16.82 | 4.547 |  | 19.76 | 0.672 | 152.7837 | 19.76 | 0 | 0 | 0 | 19.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 132.9874 | 0 | 2.8693 | 2.8693
2025-01-07 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.98 | 4.595 |  | 19.53 | 0.6726 | 154.5373 | 19.53 | 0 | 0 | 0 | 19.53 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 134.971 | 0 | 2.8693 | 2.8693
2025-01-07 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.14 | 4.641 |  | 19.3 | 0.6732 | 156.2189 | 19.3 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 136.8826 | 0 | 2.8693 | 2.8693
2025-01-07 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.29 | 4.686 |  | 19.07 | 0.6738 | 157.8629 | 19.07 | 0 | 0 | 0 | 19.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 138.7566 | 0 | 2.8693 | 2.8693
2025-01-07 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.43 | 4.729 |  | 18.85 | 0.6743 | 159.4333 | 18.85 | 0 | 0 | 0 | 18.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 140.547 | 0 | 2.8693 | 2.8693
2025-01-07 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.57 | 4.772 |  | 18.64 | 0.6748 | 161.0037 | 18.64 | 0 | 0 | 0 | 18.64 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 142.3274 | 0 | 2.8693 | 2.8693
2025-01-07 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.71 | 4.814 |  | 18.43 | 0.6753 | 162.5381 | 18.43 | 0 | 0 | 0 | 18.43 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 144.0718 | 0 | 2.8693 | 2.8693
2025-01-07 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.85 | 4.854 |  | 18.23 | 0.6757 | 164.0005 | 18.23 | 0 | 0 | 0 | 18.23 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 145.7342 | 0 | 2.8693 | 2.8693
2025-01-07 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.98 | 4.894 |  | 18.03 | 0.6762 | 165.4613 | 18.03 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 147.395 | 0 | 2.8693 | 2.8693
2025-01-07 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.11 | 4.932 |  | 17.84 | 0.6766 | 166.8501 | 17.84 | 0 | 0 | 0 | 17.84 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 148.9738 | 0 | 2.8693 | 2.8693
2025-01-07 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.23 | 4.969 |  | 17.65 | 0.677 | 168.2013 | 17.65 | 0 | 0 | 0 | 17.65 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 150.515 | 0 | 2.8693 | 2.8693
2025-01-07 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.35 | 5.005 |  | 17.47 | 0.6774 | 169.5165 | 17.47 | 0 | 0 | 0 | 17.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 152.0102 | 0 | 2.8693 | 2.8693
2025-01-07 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.47 | 5.04 |  | 17.3 | 0.6778 | 170.7957 | 17.3 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 153.4594 | 0 | 2.8693 | 2.8693
2025-01-07 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.58 | 5.073 |  | 17.13 | 0.6781 | 172.0013 | 17.13 | 0 | 0 | 0 | 17.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 154.835 | 0 | 2.8693 | 2.8693
2025-01-07 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.69 | 5.106 |  | 16.97 | 0.6784 | 173.2069 | 16.97 | 0 | 0 | 0 | 16.97 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 156.2006 | 0 | 2.8693 | 2.8693
2025-01-07 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.79 | 5.137 |  | 16.82 | 0.6788 | 174.3389 | 16.82 | 0 | 0 | 0 | 16.82 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 157.4826 | 0 | 2.8693 | 2.8693
2025-01-07 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.89 | 5.167 |  | 16.67 | 0.6791 | 175.4349 | 16.67 | 0 | 0 | 0 | 16.67 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 158.7286 | 0 | 2.8693 | 2.8693
2025-01-07 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.98 | 5.195 |  | 16.52 | 0.6793 | 176.4573 | 16.52 | 0 | 0 | 0 | 16.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 159.901 | 0 | 2.8693 | 2.8693
2025-01-07 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.08 | 5.223 |  | 16.39 | 0.6796 | 177.4813 | 16.39 | 0 | 0 | 0 | 16.39 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 161.055 | 0 | 2.8693 | 2.8693
2025-01-07 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.16 | 5.249 |  | 16.26 | 0.6799 | 178.4301 | 16.26 | 0 | 0 | 0 | 16.26 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 162.1338 | 0 | 2.8693 | 2.8693
2025-01-07 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.25 | 5.274 |  | 16.13 | 0.6801 | 179.3445 | 16.13 | 0 | 0 | 0 | 16.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 163.1782 | 0 | 2.8693 | 2.8693
2025-01-07 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.32 | 5.297 |  | 16.01 | 0.6803 | 180.1837 | 16.01 | 0 | 0 | 0 | 16.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 164.1374 | 0 | 2.8693 | 2.8693
2025-01-07 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.4 | 5.32 |  | 15.9 | 0.6805 | 181.0245 | 15.9 | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.0882 | 0 | 2.8693 | 2.8693
2025-01-07 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.47 | 5.341 |  | 15.8 | 0.6807 | 181.7917 | 15.8 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.9554 | 0 | 2.8693 | 2.8693
2025-01-08 | 1 | seasonal | Long-Term / Seasonal Storage | 19.54 | 5.361 |  | 15.7 | 0.6809 | 182.5229 | 15.7 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 166.7866 | 0 | 2.8693 | 2.8693
2025-01-08 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.6 | 5.379 |  | 15.6 | 0.6811 | 183.1805 | 15.6 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 167.5442 | 0 | 2.8693 | 2.8693
2025-01-08 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.65 | 5.396 |  | 15.52 | 0.6812 | 183.8005 | 15.52 | 0 | 0 | 0 | 15.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.2442 | 0 | 2.8693 | 2.8693
2025-01-08 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.71 | 5.412 |  | 15.44 | 0.6814 | 184.3861 | 15.44 | 0 | 0 | 0 | 15.44 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.9098 | 0 | 2.8693 | 2.8693
2025-01-08 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.76 | 5.427 |  | 15.37 | 0.6815 | 184.9341 | 15.37 | 0 | 0 | 0 | 15.37 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 169.5278 | 0 | 2.8693 | 2.8693
2025-01-08 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.8 | 5.44 |  | 15.3 | 0.6816 | 185.4085 | 15.3 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.0722 | 0 | 2.8693 | 2.8693
2025-01-08 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.84 | 5.452 |  | 15.24 | 0.6818 | 185.8469 | 15.24 | 0 | 0 | 0 | 15.24 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.5706 | 0 | 2.8693 | 2.8693
2025-01-08 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.88 | 5.463 |  | 15.19 | 0.6819 | 186.2493 | 15.19 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.023 | 0 | 2.8693 | 2.8693
2025-01-08 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.91 | 5.472 |  | 15.14 | 0.6819 | 186.5781 | 15.14 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.4018 | 0 | 2.8693 | 2.8693
2025-01-08 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.93 | 5.48 |  | 15.1 | 0.682 | 186.8693 | 15.1 | 0 | 0 | 0 | 15.1 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.733 | 0 | 2.8693 | 2.8693
2025-01-08 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.96 | 5.487 |  | 15.07 | 0.6821 | 187.1261 | 15.07 | 0 | 0 | 0 | 15.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.0198 | 0 | 2.8693 | 2.8693
2025-01-08 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.97 | 5.492 |  | 15.04 | 0.6821 | 187.3077 | 15.04 | 0 | 0 | 0 | 15.04 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.2314 | 0 | 2.8693 | 2.8693
2025-01-08 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.496 |  | 15.02 | 0.6822 | 187.4549 | 15.02 | 0 | 0 | 0 | 15.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.3986 | 0 | 2.8693 | 2.8693
2025-01-08 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.498 |  | 15.01 | 0.6822 | 187.5269 | 15.01 | 0 | 0 | 0 | 15.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.4806 | 0 | 2.8693 | 2.8693
2025-01-08 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 20 | 5.5 |  | 15 | 0.6822 | 187.6005 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.5642 | 0 | 2.8693 | 2.8693
2025-01-08 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 20 | 5.5 |  | 15 | 0.6822 | 187.6005 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.5642 | 0 | 2.8693 | 2.8693
2025-01-08 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.498 |  | 15.01 | 0.6822 | 187.5269 | 15.01 | 0 | 0 | 0 | 15.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.4806 | 0 | 2.8693 | 2.8693
2025-01-08 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.496 |  | 15.02 | 0.6822 | 187.4549 | 15.02 | 0 | 0 | 0 | 15.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.3986 | 0 | 2.8693 | 2.8693
2025-01-08 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.97 | 5.492 |  | 15.04 | 0.6821 | 187.3077 | 15.04 | 0 | 0 | 0 | 15.04 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.2314 | 0 | 2.8693 | 2.8693
2025-01-08 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.96 | 5.487 |  | 15.07 | 0.6821 | 187.1261 | 15.07 | 0 | 0 | 0 | 15.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.0198 | 0 | 2.8693 | 2.8693
2025-01-08 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.93 | 5.48 |  | 15.1 | 0.682 | 186.8693 | 15.1 | 0 | 0 | 0 | 15.1 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.733 | 0 | 2.8693 | 2.8693
2025-01-08 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.91 | 5.472 |  | 15.14 | 0.6819 | 186.5781 | 15.14 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.4018 | 0 | 2.8693 | 2.8693
2025-01-08 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.88 | 5.463 |  | 15.19 | 0.6819 | 186.2493 | 15.19 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.023 | 0 | 2.8693 | 2.8693
2025-01-08 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.84 | 5.452 |  | 15.24 | 0.6818 | 185.8469 | 15.24 | 0 | 0 | 0 | 15.24 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.5706 | 0 | 2.8693 | 2.8693
2025-01-09 | 1 | seasonal | Long-Term / Seasonal Storage | 19.8 | 5.44 |  | 15.3 | 0.6816 | 185.4085 | 15.3 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.0722 | 0 | 2.8693 | 2.8693
2025-01-09 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.76 | 5.427 |  | 15.37 | 0.6815 | 184.9341 | 15.37 | 0 | 0 | 0 | 15.37 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 169.5278 | 0 | 2.8693 | 2.8693
2025-01-09 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.71 | 5.412 |  | 15.44 | 0.6814 | 184.3861 | 15.44 | 0 | 0 | 0 | 15.44 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.9098 | 0 | 2.8693 | 2.8693
2025-01-09 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.65 | 5.396 |  | 15.52 | 0.6812 | 183.8005 | 15.52 | 0 | 0 | 0 | 15.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.2442 | 0 | 2.8693 | 2.8693
2025-01-09 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.6 | 5.379 |  | 15.6 | 0.6811 | 183.1805 | 15.6 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 167.5442 | 0 | 2.8693 | 2.8693
2025-01-09 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.54 | 5.361 |  | 15.7 | 0.6809 | 182.5229 | 15.7 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 166.7866 | 0 | 2.8693 | 2.8693
2025-01-09 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.47 | 5.341 |  | 15.8 | 0.6807 | 181.7917 | 15.8 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.9554 | 0 | 2.8693 | 2.8693
2025-01-09 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.4 | 5.32 |  | 15.9 | 0.6805 | 181.0245 | 15.9 | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.0882 | 0 | 2.8693 | 2.8693
2025-01-09 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.32 | 5.297 |  | 16.01 | 0.6803 | 180.1837 | 16.01 | 0 | 0 | 0 | 16.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 164.1374 | 0 | 2.8693 | 2.8693
2025-01-09 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.25 | 5.274 |  | 16.13 | 0.6801 | 179.3445 | 16.13 | 0 | 0 | 0 | 16.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 163.1782 | 0 | 2.8693 | 2.8693
2025-01-09 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.16 | 5.249 |  | 16.26 | 0.6799 | 178.4301 | 16.26 | 0 | 0 | 0 | 16.26 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 162.1338 | 0 | 2.8693 | 2.8693
2025-01-09 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.08 | 5.223 |  | 16.39 | 0.6796 | 177.4813 | 16.39 | 0 | 0 | 0 | 16.39 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 161.055 | 0 | 2.8693 | 2.8693
2025-01-09 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.98 | 5.195 |  | 16.52 | 0.6793 | 176.4573 | 16.52 | 0 | 0 | 0 | 16.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 159.901 | 0 | 2.8693 | 2.8693
2025-01-09 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.89 | 5.167 |  | 16.67 | 0.6791 | 175.4349 | 16.67 | 0 | 0 | 0 | 16.67 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 158.7286 | 0 | 2.8693 | 2.8693
2025-01-09 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.79 | 5.137 |  | 16.82 | 0.6788 | 174.3389 | 16.82 | 0 | 0 | 0 | 16.82 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 157.4826 | 0 | 2.8693 | 2.8693
2025-01-09 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.69 | 5.106 |  | 16.97 | 0.6784 | 173.2069 | 16.97 | 0 | 0 | 0 | 16.97 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 156.2006 | 0 | 2.8693 | 2.8693
2025-01-09 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.58 | 5.073 |  | 17.13 | 0.6781 | 172.0013 | 17.13 | 0 | 0 | 0 | 17.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 154.835 | 0 | 2.8693 | 2.8693
2025-01-09 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.47 | 5.04 |  | 17.3 | 0.6778 | 170.7957 | 17.3 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 153.4594 | 0 | 2.8693 | 2.8693
2025-01-09 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.35 | 5.005 |  | 17.47 | 0.6774 | 169.5165 | 17.47 | 0 | 0 | 0 | 17.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 152.0102 | 0 | 2.8693 | 2.8693
2025-01-09 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.23 | 4.969 |  | 17.65 | 0.677 | 168.2013 | 17.65 | 0 | 0 | 0 | 17.65 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 150.515 | 0 | 2.8693 | 2.8693
2025-01-09 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.11 | 4.932 |  | 17.84 | 0.6766 | 166.8501 | 17.84 | 0 | 0 | 0 | 17.84 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 148.9738 | 0 | 2.8693 | 2.8693
2025-01-09 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.98 | 4.894 |  | 18.03 | 0.6762 | 165.4613 | 18.03 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 147.395 | 0 | 2.8693 | 2.8693
2025-01-09 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.85 | 4.854 |  | 18.23 | 0.6757 | 164.0005 | 18.23 | 0 | 0 | 0 | 18.23 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 145.7342 | 0 | 2.8693 | 2.8693
2025-01-09 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.71 | 4.814 |  | 18.43 | 0.6753 | 162.5381 | 18.43 | 0 | 0 | 0 | 18.43 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 144.0718 | 0 | 2.8693 | 2.8693
2025-01-10 | 1 | seasonal | Long-Term / Seasonal Storage | 17.57 | 4.772 |  | 18.64 | 0.6748 | 161.0037 | 18.64 | 0 | 0 | 0 | 18.64 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 142.3274 | 0 | 2.8693 | 2.8693
2025-01-10 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.43 | 4.729 |  | 18.85 | 0.6743 | 159.4333 | 18.85 | 0 | 0 | 0 | 18.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 140.547 | 0 | 2.8693 | 2.8693
2025-01-10 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.29 | 4.686 |  | 19.07 | 0.6738 | 157.8629 | 19.07 | 0 | 0 | 0 | 19.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 138.7566 | 0 | 2.8693 | 2.8693
2025-01-10 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.14 | 4.641 |  | 19.3 | 0.6732 | 156.2189 | 19.3 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 136.8826 | 0 | 2.8693 | 2.8693
2025-01-10 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.98 | 4.595 |  | 19.53 | 0.6726 | 154.5373 | 19.53 | 0 | 0 | 0 | 19.53 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 134.971 | 0 | 2.8693 | 2.8693
2025-01-10 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.82 | 4.547 |  | 19.76 | 0.672 | 152.7837 | 19.76 | 0 | 0 | 0 | 19.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 132.9874 | 0 | 2.8693 | 2.8693
2025-01-10 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.66 | 4.499 |  | 20 | 0.6714 | 151.0301 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 130.9938 | 0 | 2.8693 | 2.8693
2025-01-10 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.5 | 4.45 |  | 20.25 | 0.6707 | 149.2405 | 20.25 | 0 | 0 | 0 | 20.25 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 128.9542 | 0 | 2.8693 | 2.8693
2025-01-10 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.33 | 4.4 |  | 20.5 | 0.6701 | 147.4133 | 20.5 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 126.877 | 0 | 2.8693 | 2.8693
2025-01-10 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.16 | 4.348 |  | 20.76 | 0.6693 | 145.5141 | 20.76 | 0 | 0 | 0 | 20.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 124.7178 | 0 | 2.8693 | 2.8693
2025-01-10 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.99 | 4.296 |  | 21.02 | 0.6686 | 143.6149 | 21.02 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 122.5586 | 0 | 2.8693 | 2.8693
2025-01-10 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.81 | 4.243 |  | 21.28 | 0.6678 | 141.6781 | 21.28 | 0 | 0 | 0 | 21.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 120.3618 | 0 | 2.8693 | 2.8693
2025-01-10 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.63 | 4.189 |  | 21.56 | 0.667 | 139.7053 | 21.56 | 0 | 0 | 0 | 21.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 118.109 | 0 | 2.8693 | 2.8693
2025-01-10 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.45 | 4.134 |  | 21.83 | 0.6662 | 137.6965 | 21.83 | 0 | 0 | 0 | 21.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 115.8302 | 0 | 2.8693 | 2.8693
2025-01-10 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.26 | 4.078 |  | 22.11 | 0.6653 | 135.6501 | 22.11 | 0 | 0 | 0 | 22.11 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 113.5038 | 0 | 2.8693 | 2.8693
2025-01-10 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.07 | 4.021 |  | 22.4 | 0.6644 | 133.5677 | 22.4 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 111.1314 | 0 | 2.8693 | 2.8693
2025-01-10 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.88 | 3.963 |  | 22.69 | 0.6634 | 131.4493 | 22.69 | 0 | 0 | 0 | 22.69 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 108.723 | 0 | 2.8693 | 2.8693
2025-01-10 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.68 | 3.904 |  | 22.98 | 0.6624 | 129.2933 | 22.98 | 0 | 0 | 0 | 22.98 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 106.277 | 0 | 2.8693 | 2.8693
2025-01-10 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.48 | 3.844 |  | 23.28 | 0.6613 | 127.1013 | 23.28 | 0 | 0 | 0 | 23.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 103.785 | 0 | 2.8693 | 2.8693
2025-01-10 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.28 | 3.784 |  | 23.58 | 0.6602 | 124.9093 | 23.58 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 101.293 | 0 | 2.8693 | 2.8693
2025-01-10 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.08 | 3.723 |  | 23.89 | 0.659 | 122.6813 | 23.89 | 0 | 0 | 0 | 23.89 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 98.755 | 0 | 2.8693 | 2.8693
2025-01-10 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.87 | 3.661 |  | 24.2 | 0.6578 | 120.4157 | 24.2 | 0 | 0 | 0 | 24.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 96.1794 | 0 | 2.8693 | 2.8693
2025-01-10 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.66 | 3.598 |  | 24.51 | 0.6566 | 118.1141 | 24.51 | 0 | 0 | 0 | 24.51 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 93.5678 | 0 | 2.8693 | 2.8693
2025-01-10 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.45 | 3.534 |  | 24.83 | 0.6552 | 115.7765 | 24.83 | 0 | 0 | 0 | 24.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 90.9102 | 0 | 2.8693 | 2.8693
2025-01-11 | 1 | seasonal | Long-Term / Seasonal Storage | 13.23 | 3.47 |  | 25.15 | 0.6538 | 113.4373 | 25.15 | 0 | 0 | 0 | 25.15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 88.251 | 0 | 2.8693 | 2.8693
2025-01-11 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.02 | 3.405 |  | 25.48 | 0.6524 | 111.0637 | 25.48 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 85.5474 | 0 | 2.8693 | 2.8693
2025-01-11 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.8 | 3.339 |  | 25.81 | 0.6508 | 108.6525 | 25.81 | 0 | 0 | 0 | 25.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 82.8062 | 0 | 2.8693 | 2.8693
2025-01-11 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.57 | 3.272 |  | 26.14 | 0.6492 | 106.2037 | 26.14 | 0 | 0 | 0 | 26.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 80.0274 | 0 | 2.8693 | 2.8693
2025-01-11 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.35 | 3.205 |  | 26.47 | 0.6475 | 103.7565 | 26.47 | 0 | 0 | 0 | 26.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 77.2502 | 0 | 2.8693 | 2.8693
2025-01-11 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.12 | 3.137 |  | 26.81 | 0.6457 | 101.2717 | 26.81 | 0 | 0 | 0 | 26.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 74.4254 | 0 | 2.8693 | 2.8693
2025-01-11 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.9 | 3.069 |  | 27.16 | 0.6438 | 98.7885 | 27.16 | 0 | 0 | 0 | 27.16 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 71.5922 | 0 | 2.8693 | 2.8693
2025-01-11 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.67 | 3 |  | 27.5 | 0.6418 | 96.2677 | 27.5 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 68.7314 | 0 | 2.8693 | 2.8693
2025-01-11 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.43 | 2.93 |  | 27.85 | 0.6397 | 93.7093 | 27.85 | 0 | 0 | 0 | 27.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 65.823 | 0 | 2.8693 | 2.8693
2025-01-11 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.2 | 2.86 |  | 28.2 | 0.6374 | 91.1525 | 28.2 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 62.9162 | 0 | 2.8693 | 2.8693
2025-01-11 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.96 | 2.789 |  | 28.56 | 0.6351 | 88.5581 | 28.56 | 0 | 0 | 0 | 28.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 59.9618 | 0 | 2.8693 | 2.8693
2025-01-11 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.73 | 2.718 |  | 28.91 | 0.6326 | 85.9653 | 28.91 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 57.019 | 0 | 2.8693 | 2.8693
2025-01-11 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.49 | 2.646 |  | 29.27 | 0.6299 | 83.3349 | 29.27 | 0 | 0 | 0 | 29.27 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 54.0286 | 0 | 2.8693 | 2.8693
2025-01-11 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.24 | 2.573 |  | 29.63 | 0.627 | 80.6669 | 29.63 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 51.0006 | 0 | 2.8693 | 2.8693
2025-01-11 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10 | 2.501 |  | 30 | 0.624 | 78.0365 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 48.0002 | 0 | 2.8693 | 2.8693
2025-01-11 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.76 | 2.427 |  | 30.36 | 0.6208 | 75.3341 | 30.36 | 0 | 0 | 0 | 30.36 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 44.9378 | 0 | 2.8693 | 2.8693
2025-01-11 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.51 | 2.354 |  | 30.73 | 0.6174 | 72.6661 | 30.73 | 0 | 0 | 0 | 30.73 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 41.8998 | 0 | 2.8693 | 2.8693
2025-01-11 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.27 | 2.28 |  | 31.1 | 0.6137 | 69.9637 | 31.1 | 0 | 0 | 0 | 31.1 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 38.8274 | 0 | 2.8693 | 2.8693
2025-01-11 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.02 | 2.205 |  | 31.47 | 0.6097 | 67.2237 | 31.47 | 0 | 0 | 0 | 31.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 35.7174 | 0 | 2.8693 | 2.8693
2025-01-11 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.77 | 2.13 |  | 31.85 | 0.6055 | 64.4837 | 31.85 | 0 | 0 | 0 | 31.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 32.5974 | 0 | 2.8693 | 2.8693
2025-01-11 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.52 | 2.055 |  | 32.22 | 0.6009 | 61.7437 | 32.22 | 0 | 0 | 0 | 32.22 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 29.4874 | 0 | 2.8693 | 2.8693
2025-01-11 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.27 | 1.98 |  | 32.6 | 0.596 | 59.0037 | 32.6 | 0 | 0 | 0 | 32.6 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 26.3674 | 0 | 2.8693 | 2.8693
2025-01-11 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.01 | 1.904 |  | 32.98 | 0.5906 | 56.2261 | 32.98 | 0 | 0 | 0 | 32.98 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 23.2098 | 0 | 2.8693 | 2.8693
2025-01-11 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.76 | 1.828 |  | 33.36 | 0.5848 | 53.4501 | 33.36 | 0 | 0 | 0 | 33.36 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 20.0538 | 0 | 2.8693 | 2.8693
2025-01-12 | 1 | seasonal | Long-Term / Seasonal Storage | 7.51 | 1.752 |  | 33.74 | 0.5785 | 50.6741 | 33.74 | 0 | 0 | 0 | 33.74 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 16.8978 | 0 | 2.8693 | 2.8693
2025-01-12 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.25 | 1.675 |  | 34.12 | 0.5715 | 47.8605 | 34.12 | 0 | 0 | 0 | 34.12 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 13.7042 | 0 | 2.8693 | 2.8693
2025-01-12 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7 | 1.599 |  | 34.51 | 0.5639 | 45.0845 | 34.51 | 0 | 0 | 0 | 34.51 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 10.5382 | 0 | 2.8693 | 2.8693
2025-01-12 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.74 | 1.522 |  | 34.89 | 0.5555 | 42.2709 | 34.89 | 0 | 0 | 0 | 34.89 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 7.3446 | 0 | 2.8693 | 2.8693
2025-01-12 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.48 | 1.445 |  | 35.28 | 0.5461 | 39.4573 | 35.28 | 0 | 0 | 0 | 35.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 4.141 | 0 | 2.8693 | 2.8693
2025-01-12 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.23 | 1.368 |  | 35.66 | 0.5358 | 36.6453 | 35.66 | 0 | 0 | 0 | 35.66 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 0.949 | 0 | 2.8693 | 2.8693
2025-01-12 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.97 | 1.29 |  | 36.05 | 0.524 | 33.7957 | 33.7957 | 2.2543 | 0 | 0 | 36.05 | 0 | 0 | 0 | 79.9969 | 79.7997 | 79.9969 | 79.9969 | 79.9937 | 77.6652 | 578.5065 | 0 | 2.2543 | 0 | 2.2543 | 0.0362 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.71 | 1.213 |  | 36.44 | 0.5108 | 30.9826 | 30.9826 | 5.4574 | 0 | 0 | 36.44 | 0 | 0 | 0 | 79.7997 | 79.3268 | 79.9937 | 77.6652 | 79.9906 | 74.3535 | 573.0133 | 0 | 5.4574 | 0 | 5.4574 | 0.0358 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.45 | 1.136 |  | 36.82 | 0.4959 | 28.1695 | 28.1695 | 8.6505 | 0 | 0 | 36.82 | 0 | 0 | 0 | 79.3268 | 78.5791 | 79.9906 | 74.3535 | 79.9875 | 71.0521 | 564.3275 | 0 | 8.6505 | 0 | 8.6505 | 0.0353 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.19 | 1.058 |  | 37.21 | 0.4786 | 25.3204 | 25.3204 | 11.8896 | 0 | 0 | 37.21 | 0 | 0 | 0 | 78.5791 | 77.5527 | 79.9875 | 71.0521 | 79.9844 | 67.7032 | 552.4033 | 0 | 11.8896 | 0 | 11.8896 | 0.0346 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.94 | 1 |  | 37.6 | 0.4639 | 23.1929 | 23.1929 | 14.4071 | 0 | 0 | 37.6 | 0 | 0 | 0 | 77.5527 | 76.3095 | 79.9844 | 67.7032 | 79.9812 | 65.0997 | 537.9626 | 0 | 14.4071 | 0 | 14.4071 | 0.0336 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.68 | 1 |  | 37.98 | 0.463 | 23.1518 | 23.1518 | 14.8282 | 0 | 0 | 37.98 | 0 | 0 | 0 | 76.3095 | 75.0303 | 79.9812 | 65.0997 | 79.9781 | 64.6616 | 523.1017 | 0 | 14.8282 | 0 | 14.8282 | 0.0327 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.42 | 1 |  | 38.37 | 0.4622 | 23.1107 | 23.1107 | 15.2593 | 0 | 0 | 38.37 | 0 | 0 | 0 | 75.0303 | 73.714 | 79.9781 | 64.6616 | 79.975 | 64.2131 | 507.8106 | 0 | 15.2593 | 0 | 15.2593 | 0.0318 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.16 | 1 |  | 38.76 | 0.4614 | 23.0696 | 23.0696 | 15.6904 | 0 | 0 | 38.76 | 0 | 0 | 0 | 73.714 | 72.3606 | 79.975 | 64.2131 | 79.9719 | 63.7647 | 492.0894 | 0 | 15.6904 | 0 | 15.6904 | 0.0308 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.9 | 1 |  | 39.14 | 0.4606 | 23.0285 | 23.0285 | 16.1115 | 0 | 0 | 39.14 | 0 | 0 | 0 | 72.3606 | 70.9711 | 79.9719 | 63.7647 | 79.9687 | 63.3266 | 475.9482 | 0 | 16.1115 | 0 | 16.1115 | 0.0298 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.65 | 1 |  | 39.53 | 0.4598 | 22.989 | 22.989 | 16.541 | 0 | 0 | 39.53 | 0 | 0 | 0 | 70.9711 | 69.5448 | 79.9687 | 63.3266 | 79.9656 | 62.8799 | 459.3784 | 0 | 16.541 | 0 | 16.541 | 0.0287 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.39 | 1 |  | 39.92 | 0.459 | 22.9479 | 22.9479 | 16.9721 | 0 | 0 | 39.92 | 0 | 0 | 0 | 69.5448 | 68.0814 | 79.9656 | 62.8799 | 79.9625 | 62.4314 | 442.3787 | 0 | 16.9721 | 0 | 16.9721 | 0.0277 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.13 | 1 |  | 40.3 | 0.4581 | 22.9068 | 22.9068 | 17.3932 | 0 | 0 | 40.3 | 0 | 0 | 0 | 68.0814 | 66.5818 | 79.9625 | 62.4314 | 77.6324 | 61.9933 | 424.9589 | 0 | 17.3932 | 0 | 17.3932 | 0.0266 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.88 | 1 |  | 40.68 | 0.4648 | 23.2396 | 23.2396 | 17.4404 | 0 | 0 | 40.68 | 0 | 0 | 0 | 66.5818 | 65.0783 | 77.6324 | 61.9933 | 74.323 | 59.6147 | 407.493 | 0 | 17.4404 | 0 | 17.4404 | 0.0255 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.62 | 1 |  | 41.07 | 0.4746 | 23.7275 | 23.7275 | 17.3425 | 0 | 0 | 41.07 | 0 | 0 | 0 | 65.0783 | 63.5833 | 74.323 | 59.6147 | 71.0239 | 56.4066 | 390.1261 | 0 | 17.3425 | 0 | 17.3425 | 0.0244 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.37 | 1 |  | 41.45 | 0.4843 | 24.2154 | 24.2154 | 17.2346 | 0 | 0 | 41.45 | 0 | 0 | 0 | 63.5833 | 62.0977 | 71.0239 | 56.4066 | 67.6773 | 53.2191 | 372.8682 | 0 | 17.2346 | 0 | 17.2346 | 0.0233 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.11 | 1 |  | 41.83 | 0.4942 | 24.7092 | 24.7092 | 17.1208 | 0 | 0 | 41.83 | 0 | 0 | 0 | 62.0977 | 60.622 | 67.6773 | 53.2191 | 65.0755 | 49.9903 | 355.7252 | 0 | 17.1208 | 0 | 17.1208 | 0.0223 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.86 | 1 |  | 42.21 | 0.5017 | 25.0855 | 25.0855 | 17.1245 | 0 | 0 | 42.21 | 0 | 0 | 0 | 60.622 | 59.146 | 65.0755 | 49.9903 | 64.6377 | 47.3849 | 338.5795 | 0 | 17.1245 | 0 | 17.1245 | 0.0212 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.61 | 1 |  | 42.59 | 0.5023 | 25.1156 | 25.1156 | 17.4744 | 0 | 0 | 42.59 | 0 | 0 | 0 | 59.146 | 57.64 | 64.6377 | 47.3849 | 64.1896 | 46.5856 | 321.085 | 0 | 17.4744 | 0 | 17.4744 | 0.0201 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 | 1 | seasonal | Long-Term / Seasonal Storage | 1.36 | 1 |  | 42.96 | 0.5029 | 25.1473 | 25.1473 | 17.8127 | 0 | 0 | 42.96 | 0 | 0 | 0 | 57.64 | 56.105 | 64.1896 | 46.5856 | 63.7415 | 45.7881 | 303.2533 | 0 | 17.8127 | 0 | 17.8127 | 0.019 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.11 | 1 |  | 43.34 | 0.5036 | 25.179 | 25.179 | 18.161 | 0 | 0 | 43.34 | 0 | 0 | 0 | 56.105 | 54.5401 | 63.7415 | 45.7881 | 63.2849 | 44.9991 | 285.0744 | 0 | 18.161 | 0 | 18.161 | 0.0178 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.86 | 1 |  | 43.71 | 0.5042 | 25.212 | 25.212 | 18.498 | 0 | 0 | 43.71 | 0 | 0 | 0 | 54.5401 | 52.9463 | 63.2849 | 44.9991 | 62.4112 | 44.9981 | 266.5598 | 0 | 18.498 | 0 | 18.498 | 0.0167 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.61 | 1 |  | 44.08 | 0.5062 | 25.3118 | 25.3118 | 18.7682 | 0 | 0 | 44.08 | 0 | 0 | 0 | 52.9463 | 51.3294 | 62.4112 | 44.9981 | 61.9733 | 44.9972 | 247.7761 | 0 | 18.7682 | 0 | 18.7682 | 0.0155 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.36 | 1 |  | 44.45 | 0.5068 | 25.3419 | 25.3419 | 19.1081 | 0 | 0 | 44.45 | 0 | 0 | 0 | 51.3294 | 49.6832 | 61.9733 | 44.9972 | 59.5962 | 44.9962 | 228.6536 | 0 | 19.1081 | 0 | 19.1081 | 0.0143 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.12 | 1 |  | 44.82 | 0.5137 | 25.6838 | 25.6838 | 19.1362 | 0 | 0 | 44.82 | 0 | 0 | 0 | 49.6832 | 48.0348 | 59.5962 | 44.9962 | 56.3901 | 44.9953 | 209.5044 | 0 | 19.1362 | 0 | 19.1362 | 0.0131 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.12 | 1 |  | 45.19 | 0.5232 | 26.1584 | 26.1584 | 19.0316 | 0 | 0 | 45.19 | 0 | 0 | 0 | 48.0348 | 46.3955 | 56.3901 | 44.9953 | 52.0507 | 44.9944 | 190.4608 | 0 | 19.0316 | 0 | 19.0316 | 0.0119 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.37 | 1 |  | 45.55 | 0.5363 | 26.8127 | 26.8127 | 16.2308 | 2.5065 | 1.7904 | 45.55 | 0 | 0.7161 | 0.7161 | 46.3955 | 44.8432 | 52.0507 | 44.9944 | 44.9991 | 43.1497 | 172.4289 | 0 | 16.2308 | 1.7904 | 18.0212 | 0.0108 | 0 | 0.0859 | 2.8693 | 2.9553
2025-01-13 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.61 | 1 |  | 45.91 | 0.558 | 27.9024 | 27.9024 | 0 | 18.0076 | 12.8626 | 45.91 | 0 | 5.145 | 5.145 | 44.8432 | 43.7351 | 44.9991 | 43.1497 | 44.9981 | 34.9997 | 159.5563 | 0 | 0 | 12.8626 | 12.8626 | 0.01 | 0 | 0.6174 | 2.8693 | 3.4868
2025-01-13 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.84 | 1 |  | 46.27 | 0.5573 | 27.8656 | 27.8656 | 0 | 18.4044 | 13.146 | 46.27 | 0 | 5.2584 | 5.2584 | 43.7351 | 42.6027 | 44.9981 | 34.9997 | 44.9962 | 34.9994 | 146.4012 | 0 | 0 | 13.146 | 13.146 | 0.0092 | 0 | 0.631 | 2.8693 | 3.5004
2025-01-13 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.08 | 1 |  | 46.62 | 0.5565 | 27.8272 | 27.8272 | 0 | 18.7928 | 13.4234 | 46.62 | 0 | 5.3694 | 5.3694 | 42.6027 | 41.4464 | 44.9962 | 34.9994 | 44.9944 | 34.9991 | 132.9694 | 0 | 0 | 13.4234 | 13.4234 | 0.0083 | 0 | 0.6443 | 2.8693 | 3.5137
2025-01-13 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.32 | 1 |  | 46.97 | 0.5558 | 27.7888 | 27.7888 | 0 | 19.1812 | 13.7009 | 46.97 | 0 | 5.4803 | 5.4803 | 41.4464 | 40.2664 | 44.9944 | 34.9991 | 44.9916 | 34.9987 | 119.2611 | 0 | 0 | 13.7009 | 13.7009 | 0.0075 | 0 | 0.6576 | 2.8693 | 3.527
2025-01-13 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.55 | 1 |  | 47.32 | 0.555 | 27.752 | 27.752 | 0 | 19.568 | 13.9771 | 47.32 | 0 | 5.5909 | 5.5909 | 40.2664 | 39.0626 | 44.9916 | 34.9987 | 44.9887 | 34.9984 | 105.2774 | 0 | 0 | 13.9771 | 13.9771 | 0.0066 | 0 | 0.6709 | 2.8693 | 3.5403
2025-01-13 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.78 | 1 |  | 47.67 | 0.5543 | 27.7152 | 27.7152 | 0 | 19.9548 | 14.2534 | 47.67 | 0 | 5.7014 | 5.7014 | 39.0626 | 37.8351 | 44.9887 | 34.9984 | 41.7067 | 34.9981 | 91.0183 | 0 | 0 | 14.2534 | 14.2534 | 0.0057 | 0 | 0.6842 | 2.8693 | 3.5535
2025-01-13 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.01 | 1 |  | 48.02 | 0.5536 | 27.6784 | 27.6784 | 0 | 20.3416 | 14.5297 | 48.02 | 0 | 5.8119 | 5.8119 | 37.8351 | 36.584 | 41.7067 | 34.9981 | 40.8321 | 34.9978 | 76.4838 | 0 | 0 | 14.5297 | 14.5297 | 0.0048 | 0 | 0.6974 | 2.8693 | 3.5668
2025-01-13 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.24 | 1 |  | 48.36 | 0.5528 | 27.6416 | 27.6416 | 0 | 20.7184 | 14.7989 | 48.36 | 0 | 5.9195 | 5.9195 | 36.584 | 35.3097 | 40.8321 | 34.9978 | 38.409 | 34.9975 | 61.6811 | 0 | 0 | 14.7989 | 14.7989 | 0.0039 | 0 | 0.7103 | 2.8693 | 3.5797
2025-01-13 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.46 | 1 |  | 48.69 | 0.5521 | 27.6064 | 27.6064 | 0 | 5.0533 | 3.6095 | 32.6597 | 16.0303 | 6.0239 | 1.4438 | 35.3097 | 34.9987 | 38.409 | 34.9975 | 34.9997 | 34.9972 | 58.0679 | 0 | 0 | 3.6095 | 3.6095 | 0.0036 | 0 | 0.7229 | 2.8693 | 3.5922
2025-01-13 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.69 | 1 |  | 49.03 | 0.5514 | 27.5696 | 27.5696 | 0 | 0 | 0 | 27.5696 | 21.4604 | 6.1315 | 0 | 34.9987 | 34.9984 | 34.9997 | 34.9972 | 34.9994 | 34.9969 | 58.0643 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7358 | 2.8693 | 3.6051
2025-01-13 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.91 | 1 |  | 49.36 | 0.5507 | 27.5344 | 27.5344 | 0 | 0 | 0 | 27.5344 | 21.8256 | 6.2359 | 0 | 34.9984 | 34.998 | 34.9994 | 34.9969 | 34.9991 | 34.9966 | 58.0606 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7483 | 2.8693 | 3.6177
2025-01-13 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.12 | 1 |  | 49.69 | 0.55 | 27.5008 | 27.5008 | 0 | 0 | 0 | 27.5008 | 22.1892 | 6.3398 | 0 | 34.998 | 34.9977 | 34.9991 | 34.9966 | 34.9987 | 34.9962 | 58.057 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7608 | 2.8693 | 3.6301
2025-01-13 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.34 | 1 |  | 50.01 | 0.5493 | 27.4656 | 27.4656 | 0 | 0 | 0 | 27.4656 | 22.5444 | 6.4413 | 0 | 34.9977 | 34.9974 | 34.9987 | 34.9962 | 34.9984 | 34.9959 | 58.0534 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.773 | 2.8693 | 3.6423
2025-01-13 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.55 | 1 |  | 50.33 | 0.5486 | 27.432 | 27.432 | 0 | 0 | 0 | 27.432 | 22.898 | 6.5423 | 0 | 34.9974 | 34.9971 | 34.9984 | 34.9959 | 34.9981 | 34.9956 | 58.0497 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7851 | 2.8693 | 3.6544
2025-01-13 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.76 | 1 |  | 50.65 | 0.548 | 27.3984 | 27.3984 | 0 | 0 | 0 | 27.3984 | 23.2516 | 6.6433 | 0 | 34.9971 | 34.9968 | 34.9981 | 34.9956 | 34.9978 | 34.9953 | 58.0461 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7972 | 2.8693 | 3.6665
2025-01-13 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.97 | 1 |  | 50.96 | 0.5473 | 27.3648 | 27.3648 | 0 | 0 | 0 | 27.3648 | 23.5952 | 6.7415 | 0 | 34.9968 | 34.9965 | 34.9978 | 34.9953 | 34.9975 | 34.995 | 58.0425 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.809 | 2.8693 | 3.6783
2025-01-14 | 1 | seasonal | Long-Term / Seasonal Storage | -4.18 | 1 |  | 51.27 | 0.5466 | 27.3312 | 27.3312 | 0 | 0 | 0 | 27.3312 | 23.9388 | 6.8397 | 0 | 34.9965 | 34.9962 | 34.9975 | 34.995 | 34.9972 | 34.9947 | 58.0388 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8208 | 2.8693 | 3.6901
2025-01-14 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.38 | 1 |  | 51.57 | 0.546 | 27.2992 | 27.2992 | 0 | 0 | 0 | 27.2992 | 24.2708 | 6.9345 | 0 | 34.9962 | 34.9959 | 34.9972 | 34.9947 | 34.9969 | 34.9944 | 58.0352 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8321 | 2.8693 | 3.7015
2025-01-14 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.58 | 1 |  | 51.87 | 0.5453 | 27.2672 | 27.2672 | 0 | 0 | 0 | 27.2672 | 24.6028 | 7.0294 | 0 | 34.9959 | 34.9955 | 34.9969 | 34.9944 | 34.9966 | 34.9941 | 58.0316 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8435 | 2.8693 | 3.7129
2025-01-14 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.78 | 1 |  | 52.17 | 0.5447 | 27.2352 | 27.2352 | 0 | 0 | 0 | 27.2352 | 24.9348 | 7.1242 | 0 | 34.9955 | 34.9952 | 34.9966 | 34.9941 | 34.9962 | 34.9937 | 58.028 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8549 | 2.8693 | 3.7243
2025-01-14 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.97 | 1 |  | 52.46 | 0.5441 | 27.2048 | 27.2048 | 0 | 0 | 0 | 27.2048 | 25.2552 | 7.2158 | 0 | 34.9952 | 34.9949 | 34.9962 | 34.9937 | 34.9959 | 34.9934 | 58.0243 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8659 | 2.8693 | 3.7352
2025-01-14 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.16 | 1 |  | 52.75 | 0.5435 | 27.1744 | 27.1744 | 0 | 0 | 0 | 27.1744 | 25.5756 | 7.3073 | 0 | 34.9949 | 34.9946 | 34.9959 | 34.9934 | 34.9956 | 34.9931 | 58.0207 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8769 | 2.8693 | 3.7462
2025-01-14 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.35 | 1 |  | 53.03 | 0.5429 | 27.144 | 27.144 | 0 | 0 | 0 | 27.144 | 25.886 | 7.396 | 0 | 34.9946 | 34.9943 | 34.9956 | 34.9931 | 34.9953 | 34.9928 | 58.0171 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8875 | 2.8693 | 3.7569
2025-01-14 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.54 | 1 |  | 53.31 | 0.5423 | 27.1136 | 27.1136 | 0 | 0 | 0 | 27.1136 | 26.1964 | 7.4847 | 0 | 34.9943 | 34.994 | 34.9953 | 34.9928 | 34.995 | 34.9925 | 58.0134 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8982 | 2.8693 | 3.7675
2025-01-14 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.72 | 1 |  | 53.58 | 0.5417 | 27.0848 | 27.0848 | 0 | 0 | 0 | 27.0848 | 26.4952 | 7.5701 | 0 | 34.994 | 34.9937 | 34.995 | 34.9925 | 34.9947 | 34.9922 | 58.0098 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9084 | 2.8693 | 3.7778
2025-01-14 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.9 | 1 |  | 53.85 | 0.5411 | 27.056 | 27.056 | 0 | 0 | 0 | 27.056 | 26.794 | 7.6554 | 0 | 34.9937 | 34.9934 | 34.9947 | 34.9922 | 34.9944 | 34.9919 | 58.0062 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9187 | 2.8693 | 3.788
2025-01-14 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.07 | 1 |  | 54.11 | 0.5406 | 27.0288 | 27.0288 | 0 | 0 | 0 | 27.0288 | 27.0812 | 7.7375 | 0 | 34.9934 | 34.993 | 34.9944 | 34.9919 | 34.9941 | 34.9916 | 58.0026 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9285 | 2.8693 | 3.7978
2025-01-14 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.25 | 1 |  | 54.37 | 0.54 | 27 | 27 | 0 | 0 | 0 | 27 | 27.37 | 7.82 | 0 | 34.993 | 34.9927 | 34.9941 | 34.9916 | 34.9937 | 34.9913 | 57.9989 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9384 | 2.8693 | 3.8077
2025-01-14 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.42 | 1 |  | 54.62 | 0.5395 | 26.9728 | 26.9728 | 0 | 0 | 0 | 26.9728 | 27.6472 | 7.8992 | 0 | 34.9927 | 34.9924 | 34.9937 | 34.9913 | 34.9934 | 34.9909 | 57.9953 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9479 | 2.8693 | 3.8173
2025-01-14 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.58 | 1 |  | 54.87 | 0.5389 | 26.9472 | 26.9472 | 0 | 0 | 0 | 26.9472 | 27.9228 | 7.9779 | 0 | 34.9924 | 34.9921 | 34.9934 | 34.9909 | 34.9931 | 34.9906 | 57.9917 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9574 | 2.8693 | 3.8267
2025-01-14 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.74 | 1 |  | 55.12 | 0.5384 | 26.9216 | 26.9216 | 0 | 0 | 0 | 26.9216 | 28.1984 | 8.0567 | 0 | 34.9921 | 34.9918 | 34.9931 | 34.9906 | 34.9928 | 34.9903 | 57.988 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9668 | 2.8693 | 3.8362
2025-01-14 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.9 | 1 |  | 55.36 | 0.5379 | 26.896 | 26.896 | 0 | 0 | 0 | 26.896 | 28.464 | 8.1326 | 0 | 34.9918 | 34.9915 | 34.9928 | 34.9903 | 34.9925 | 34.99 | 57.9844 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9759 | 2.8693 | 3.8453
2025-01-14 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.06 | 1 |  | 55.59 | 0.5374 | 26.8704 | 26.8704 | 0 | 0 | 0 | 26.8704 | 28.7196 | 8.2056 | 0 | 34.9915 | 34.9912 | 34.9925 | 34.99 | 34.9922 | 34.9897 | 57.9808 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9847 | 2.8693 | 3.854
2025-01-14 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.21 | 1 |  | 55.82 | 0.5369 | 26.8464 | 26.8464 | 0 | 0 | 0 | 26.8464 | 28.9736 | 8.2782 | 0 | 34.9912 | 34.9909 | 34.9922 | 34.9897 | 34.9919 | 34.9894 | 57.9772 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9934 | 2.8693 | 3.8627
2025-01-14 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.36 | 1 |  | 56.04 | 0.5364 | 26.8224 | 26.8224 | 0 | 0 | 0 | 26.8224 | 29.2176 | 8.3479 | 0 | 34.9909 | 34.9905 | 34.9919 | 34.9894 | 34.9916 | 34.9891 | 57.9735 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0017 | 2.8693 | 3.8711
2025-01-14 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.5 | 1 |  | 56.26 | 0.536 | 26.8 | 26.8 | 0 | 0 | 0 | 26.8 | 29.46 | 8.4171 | 0 | 34.9905 | 34.9902 | 34.9916 | 34.9891 | 34.9913 | 34.9888 | 57.9699 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0101 | 2.8693 | 3.8794
2025-01-14 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.64 | 1 |  | 56.47 | 0.5356 | 26.7776 | 26.7776 | 0 | 0 | 0 | 26.7776 | 29.6924 | 8.4835 | 0 | 34.9902 | 34.9899 | 34.9913 | 34.9888 | 34.9909 | 34.9884 | 57.9663 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.018 | 2.8693 | 3.8874
2025-01-14 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.78 | 1 |  | 56.67 | 0.5351 | 26.7552 | 26.7552 | 0 | 0 | 0 | 26.7552 | 29.9148 | 8.5471 | 0 | 34.9899 | 34.9896 | 34.9909 | 34.9884 | 34.9906 | 34.9881 | 57.9627 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0257 | 2.8693 | 3.895
2025-01-14 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.91 | 1 |  | 56.87 | 0.5347 | 26.7344 | 26.7344 | 0 | 0 | 0 | 26.7344 | 30.1356 | 8.6102 | 0 | 34.9896 | 34.9893 | 34.9906 | 34.9881 | 34.9903 | 34.9878 | 57.959 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0332 | 2.8693 | 3.9026
2025-01-14 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.04 | 1 |  | 57.07 | 0.5343 | 26.7136 | 26.7136 | 0 | 0 | 0 | 26.7136 | 30.3564 | 8.6733 | 0 | 34.9893 | 34.989 | 34.9903 | 34.9878 | 34.99 | 34.9875 | 57.9554 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0408 | 2.8693 | 3.9101
2025-01-15 | 1 | seasonal | Long-Term / Seasonal Storage | -8.17 | 1 |  | 57.25 | 0.5339 | 26.6928 | 26.6928 | 0 | 0 | 0 | 26.6928 | 30.5572 | 8.7306 | 0 | 34.989 | 34.9887 | 34.99 | 34.9875 | 34.9897 | 34.9872 | 57.9518 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0477 | 2.8693 | 3.917
2025-01-15 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.29 | 1 |  | 57.44 | 0.5335 | 26.6736 | 26.6736 | 0 | 0 | 0 | 26.6736 | 30.7664 | 8.7904 | 0 | 34.9887 | 34.9884 | 34.9897 | 34.9872 | 34.9894 | 34.9869 | 57.9482 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0548 | 2.8693 | 3.9242
2025-01-15 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.41 | 1 |  | 57.61 | 0.5331 | 26.6544 | 26.6544 | 0 | 0 | 0 | 26.6544 | 30.9556 | 8.8445 | 0 | 34.9884 | 34.9881 | 34.9894 | 34.9869 | 34.9891 | 34.9866 | 57.9445 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0613 | 2.8693 | 3.9307
2025-01-15 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.52 | 1 |  | 57.78 | 0.5327 | 26.6368 | 26.6368 | 0 | 0 | 0 | 26.6368 | 31.1432 | 8.8981 | 0 | 34.9881 | 34.9877 | 34.9891 | 34.9866 | 34.9888 | 34.9863 | 57.9409 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0678 | 2.8693 | 3.9371
2025-01-15 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.63 | 1 |  | 57.95 | 0.5324 | 26.6192 | 26.6192 | 0 | 0 | 0 | 26.6192 | 31.3308 | 8.9517 | 0 | 34.9877 | 34.9874 | 34.9888 | 34.9863 | 34.9884 | 34.9859 | 57.9373 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0742 | 2.8693 | 3.9435
2025-01-15 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.74 | 1 |  | 58.11 | 0.532 | 26.6016 | 26.6016 | 0 | 0 | 0 | 26.6016 | 31.5084 | 9.0024 | 0 | 34.9874 | 34.9871 | 34.9884 | 34.9859 | 34.9881 | 34.9856 | 57.9337 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0803 | 2.8693 | 3.9496
2025-01-15 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.84 | 1 |  | 58.26 | 0.5317 | 26.5856 | 26.5856 | 0 | 0 | 0 | 26.5856 | 31.6744 | 9.0498 | 0 | 34.9871 | 34.9868 | 34.9881 | 34.9856 | 34.9878 | 34.9853 | 57.93 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.086 | 2.8693 | 3.9553
2025-01-15 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.94 | 1 |  | 58.41 | 0.5314 | 26.5696 | 26.5696 | 0 | 0 | 0 | 26.5696 | 31.8404 | 9.0973 | 0 | 34.9868 | 34.9865 | 34.9878 | 34.9853 | 34.9875 | 34.985 | 57.9264 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0917 | 2.8693 | 3.961
2025-01-15 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.03 | 1 |  | 58.55 | 0.5311 | 26.5552 | 26.5552 | 0 | 0 | 0 | 26.5552 | 31.9948 | 9.1414 | 0 | 34.9865 | 34.9862 | 34.9875 | 34.985 | 34.9872 | 34.9847 | 57.9228 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.097 | 2.8693 | 3.9663
2025-01-15 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.12 | 1 |  | 58.68 | 0.5308 | 26.5408 | 26.5408 | 0 | 0 | 0 | 26.5408 | 32.1392 | 9.1826 | 0 | 34.9862 | 34.9859 | 34.9872 | 34.9847 | 34.9869 | 34.9844 | 57.9192 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1019 | 2.8693 | 3.9713
2025-01-15 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.2 | 1 |  | 58.81 | 0.5306 | 26.528 | 26.528 | 0 | 0 | 0 | 26.528 | 32.282 | 9.2234 | 0 | 34.9859 | 34.9856 | 34.9869 | 34.9844 | 34.9866 | 34.9841 | 57.9156 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1068 | 2.8693 | 3.9762
2025-01-15 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.29 | 1 |  | 58.93 | 0.5303 | 26.5136 | 26.5136 | 0 | 0 | 0 | 26.5136 | 32.4164 | 9.2618 | 0 | 34.9856 | 34.9852 | 34.9866 | 34.9841 | 34.9863 | 34.9838 | 57.9119 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1114 | 2.8693 | 3.9808
2025-01-15 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.36 | 1 |  | 59.04 | 0.53 | 26.5024 | 26.5024 | 0 | 0 | 0 | 26.5024 | 32.5376 | 9.2965 | 0 | 34.9852 | 34.9849 | 34.9863 | 34.9838 | 34.9859 | 34.9835 | 57.9083 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1156 | 2.8693 | 3.9849
2025-01-15 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.43 | 1 |  | 59.15 | 0.5298 | 26.4912 | 26.4912 | 0 | 0 | 0 | 26.4912 | 32.6588 | 9.3311 | 0 | 34.9849 | 34.9846 | 34.9859 | 34.9835 | 34.9856 | 34.9831 | 57.9047 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1197 | 2.8693 | 3.9891
2025-01-15 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.5 | 1 |  | 59.25 | 0.5296 | 26.48 | 26.48 | 0 | 0 | 0 | 26.48 | 32.77 | 9.3629 | 0 | 34.9846 | 34.9843 | 34.9856 | 34.9831 | 34.9853 | 34.9828 | 57.9011 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1235 | 2.8693 | 3.9929
2025-01-15 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.57 | 1 |  | 59.35 | 0.5294 | 26.4688 | 26.4688 | 0 | 0 | 0 | 26.4688 | 32.8812 | 9.3946 | 0 | 34.9843 | 34.984 | 34.9853 | 34.9828 | 34.985 | 34.9825 | 57.8974 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1274 | 2.8693 | 3.9967
2025-01-15 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.63 | 1 |  | 59.44 | 0.5292 | 26.4592 | 26.4592 | 0 | 0 | 0 | 26.4592 | 32.9808 | 9.4231 | 0 | 34.984 | 34.9837 | 34.985 | 34.9825 | 34.9847 | 34.9822 | 57.8938 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1308 | 2.8693 | 4.0001
2025-01-15 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.68 | 1 |  | 59.52 | 0.529 | 26.4512 | 26.4512 | 0 | 0 | 0 | 26.4512 | 33.0688 | 9.4482 | 0 | 34.9837 | 34.9834 | 34.9847 | 34.9822 | 34.9844 | 34.9819 | 57.8902 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1338 | 2.8693 | 4.0031
2025-01-15 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.73 | 1 |  | 59.6 | 0.5289 | 26.4432 | 26.4432 | 0 | 0 | 0 | 26.4432 | 33.1568 | 9.4734 | 0 | 34.9834 | 34.9831 | 34.9844 | 34.9819 | 34.9841 | 34.9816 | 57.8866 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1368 | 2.8693 | 4.0062
2025-01-15 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.78 | 1 |  | 59.67 | 0.5287 | 26.4352 | 26.4352 | 0 | 0 | 0 | 26.4352 | 33.2348 | 9.4957 | 0 | 34.9831 | 34.9828 | 34.9841 | 34.9816 | 34.9838 | 34.9813 | 57.883 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1395 | 2.8693 | 4.0088
2025-01-15 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.82 | 1 |  | 59.73 | 0.5286 | 26.4288 | 26.4288 | 0 | 0 | 0 | 26.4288 | 33.3012 | 9.5146 | 0 | 34.9828 | 34.9824 | 34.9838 | 34.9813 | 34.9835 | 34.981 | 57.8793 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1418 | 2.8693 | 4.0111
2025-01-15 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.86 | 1 |  | 59.79 | 0.5284 | 26.4224 | 26.4224 | 0 | 0 | 0 | 26.4224 | 33.3676 | 9.5336 | 0 | 34.9824 | 34.9821 | 34.9835 | 34.981 | 34.9831 | 34.9806 | 57.8757 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.144 | 2.8693 | 4.0134
2025-01-15 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.89 | 1 |  | 59.84 | 0.5284 | 26.4176 | 26.4176 | 0 | 0 | 0 | 26.4176 | 33.4224 | 9.5493 | 0 | 34.9821 | 34.9818 | 34.9831 | 34.9806 | 34.9828 | 34.9803 | 57.8721 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1459 | 2.8693 | 4.0153
2025-01-15 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.92 | 1 |  | 59.88 | 0.5283 | 26.4128 | 26.4128 | 0 | 0 | 0 | 26.4128 | 33.4672 | 9.5621 | 0 | 34.9818 | 34.9815 | 34.9828 | 34.9803 | 34.9825 | 34.98 | 57.8685 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1474 | 2.8693 | 4.0168
2025-01-16 | 1 | seasonal | Long-Term / Seasonal Storage | -9.94 | 1 |  | 59.92 | 0.5282 | 26.4096 | 26.4096 | 0 | 0 | 0 | 26.4096 | 33.5104 | 9.5744 | 0 | 34.9815 | 34.9812 | 34.9825 | 34.98 | 34.9822 | 34.9797 | 57.8649 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1489 | 2.8693 | 4.0183
2025-01-16 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.96 | 1 |  | 59.95 | 0.5281 | 26.4064 | 26.4064 | 0 | 0 | 0 | 26.4064 | 33.5436 | 9.5839 | 0 | 34.9812 | 34.9809 | 34.9822 | 34.9797 | 34.9819 | 34.9794 | 57.8612 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1501 | 2.8693 | 4.0194
2025-01-16 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.98 | 1 |  | 59.97 | 0.5281 | 26.4032 | 26.4032 | 0 | 0 | 0 | 26.4032 | 33.5668 | 9.5905 | 0 | 34.9809 | 34.9806 | 34.9819 | 34.9794 | 34.9816 | 34.9791 | 57.8576 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1509 | 2.8693 | 4.0202
2025-01-16 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.99 | 1 |  | 59.99 | 0.528 | 26.4016 | 26.4016 | 0 | 0 | 0 | 26.4016 | 33.5884 | 9.5967 | 0 | 34.9806 | 34.9803 | 34.9816 | 34.9791 | 34.9813 | 34.9788 | 57.854 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1516 | 2.8693 | 4.021
2025-01-16 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -10 | 1 |  | 60 | 0.528 | 26.4 | 26.4 | 0 | 0 | 0 | 26.4 | 33.6 | 9.6 | 0 | 34.9803 | 34.9799 | 34.9813 | 34.9788 | 34.981 | 34.9785 | 57.8504 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.152 | 2.8693 | 4.0213

## Final_Selected_Monthly
month | heating_load_kwh | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated
2025-01 | 13687.6 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 4042.8779 | 1201.5447 | 529.0192 | 522.0303 | 7.2218 | 144.1854 | 1047.3121 | 1191.4974

## Final_Selected_Annual
period | heating_load_kwh | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated | annualized_total_cost | solar_coverage_pct
annual | 13687.6 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 4042.8779 | 1201.5447 | 529.0192 | 522.0303 | 7.2218 | 144.1854 | 1047.3121 | 1191.4974 | 1191.4974 | 70.4632

## Optimized_Summary
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct
seasonal | Long-Term / Seasonal Storage | 50 | 10 | 580.8333 | 35 | 34.9799 | 35 | 1 | TRUE | 3 | 300 | 15000 | 5946.241 | 1047.3121 | 144.1854 | 1191.4974 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 116.0919 | 9598.2854 | 9644.7221 | 4042.8779 | 1201.5447 | 46.4367 | 18661.7779 | 529.0192 | 522.0303 | 7.2218 | 13687.6 | 70.4632 | 29.5368

## Optimized_Hourly
timestamp | simulation_year_index | tank_type | tank_type_label | outside_temp_c | solar_rad_kwh_m2 | horizontal_solar_rad_kwh_m2 | heating_load_kwh | collector_efficiency | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_heating_total_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | tank_temp_start_c | tank_temp_end_c | tank_top_temp_start_c | tank_bottom_temp_start_c | tank_top_temp_end_c | tank_bottom_temp_end_c | tank_stored_energy_kwh | tank_charge_kwh | tank_discharge_direct_kwh | tank_discharge_hp_source_kwh | tank_discharge_total_kwh | tank_loss_kwh | solar_energy_curtailed_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated
2025-01-01 | 1 | seasonal | Long-Term / Seasonal Storage | -10 | 1 |  | 60 | 0.528 | 26.4 | 26.4 | 0 | 0 | 0 | 26.4 | 33.6 | 9.6 | 0 | 35 | 34.9997 | 35 | 35 | 34.9997 | 34.9997 | 58.0797 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.152 | 2.8693 | 4.0213
2025-01-01 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -10 | 1 |  | 60 | 0.528 | 26.4 | 26.4 | 0 | 0 | 0 | 26.4 | 33.6 | 9.6 | 0 | 34.9997 | 34.9994 | 34.9997 | 34.9997 | 34.9994 | 34.9994 | 58.0761 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.152 | 2.8693 | 4.0213
2025-01-01 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.99 | 1 |  | 59.99 | 0.528 | 26.4016 | 26.4016 | 0 | 0 | 0 | 26.4016 | 33.5884 | 9.5967 | 0 | 34.9994 | 34.9991 | 34.9994 | 34.9994 | 34.9991 | 34.9991 | 58.0724 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1516 | 2.8693 | 4.021
2025-01-01 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.98 | 1 |  | 59.97 | 0.5281 | 26.4032 | 26.4032 | 0 | 0 | 0 | 26.4032 | 33.5668 | 9.5905 | 0 | 34.9991 | 34.9987 | 34.9991 | 34.9991 | 34.9987 | 34.9987 | 58.0688 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1509 | 2.8693 | 4.0202
2025-01-01 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.96 | 1 |  | 59.95 | 0.5281 | 26.4064 | 26.4064 | 0 | 0 | 0 | 26.4064 | 33.5436 | 9.5839 | 0 | 34.9987 | 34.9984 | 34.9987 | 34.9987 | 34.9984 | 34.9984 | 58.0652 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1501 | 2.8693 | 4.0194
2025-01-01 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.94 | 1 |  | 59.92 | 0.5282 | 26.4096 | 26.4096 | 0 | 0 | 0 | 26.4096 | 33.5104 | 9.5744 | 0 | 34.9984 | 34.9981 | 34.9984 | 34.9984 | 34.9981 | 34.9981 | 58.0615 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1489 | 2.8693 | 4.0183
2025-01-01 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.92 | 1 |  | 59.88 | 0.5283 | 26.4128 | 26.4128 | 0 | 0 | 0 | 26.4128 | 33.4672 | 9.5621 | 0 | 34.9981 | 34.9978 | 34.9981 | 34.9981 | 34.9978 | 34.9978 | 58.0579 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1474 | 2.8693 | 4.0168
2025-01-01 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.89 | 1 |  | 59.84 | 0.5284 | 26.4176 | 26.4176 | 0 | 0 | 0 | 26.4176 | 33.4224 | 9.5493 | 0 | 34.9978 | 34.9975 | 34.9978 | 34.9978 | 34.9975 | 34.9975 | 58.0543 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1459 | 2.8693 | 4.0153
2025-01-01 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.86 | 1 |  | 59.79 | 0.5284 | 26.4224 | 26.4224 | 0 | 0 | 0 | 26.4224 | 33.3676 | 9.5336 | 0 | 34.9975 | 34.9972 | 34.9975 | 34.9975 | 34.9972 | 34.9972 | 58.0506 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.144 | 2.8693 | 4.0134
2025-01-01 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.82 | 1 |  | 59.73 | 0.5286 | 26.4288 | 26.4288 | 0 | 0 | 0 | 26.4288 | 33.3012 | 9.5146 | 0 | 34.9972 | 34.9969 | 34.9972 | 34.9972 | 34.9969 | 34.9969 | 58.047 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1418 | 2.8693 | 4.0111
2025-01-01 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.78 | 1 |  | 59.67 | 0.5287 | 26.4352 | 26.4352 | 0 | 0 | 0 | 26.4352 | 33.2348 | 9.4957 | 0 | 34.9969 | 34.9966 | 34.9969 | 34.9969 | 34.9966 | 34.9966 | 58.0434 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1395 | 2.8693 | 4.0088
2025-01-01 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.73 | 1 |  | 59.6 | 0.5289 | 26.4432 | 26.4432 | 0 | 0 | 0 | 26.4432 | 33.1568 | 9.4734 | 0 | 34.9966 | 34.9962 | 34.9966 | 34.9966 | 34.9962 | 34.9962 | 58.0398 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1368 | 2.8693 | 4.0062
2025-01-01 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.68 | 1 |  | 59.52 | 0.529 | 26.4512 | 26.4512 | 0 | 0 | 0 | 26.4512 | 33.0688 | 9.4482 | 0 | 34.9962 | 34.9959 | 34.9962 | 34.9962 | 34.9959 | 34.9959 | 58.0361 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1338 | 2.8693 | 4.0031
2025-01-01 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.63 | 1 |  | 59.44 | 0.5292 | 26.4592 | 26.4592 | 0 | 0 | 0 | 26.4592 | 32.9808 | 9.4231 | 0 | 34.9959 | 34.9956 | 34.9959 | 34.9959 | 34.9956 | 34.9956 | 58.0325 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1308 | 2.8693 | 4.0001
2025-01-01 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.57 | 1 |  | 59.35 | 0.5294 | 26.4688 | 26.4688 | 0 | 0 | 0 | 26.4688 | 32.8812 | 9.3946 | 0 | 34.9956 | 34.9953 | 34.9956 | 34.9956 | 34.9953 | 34.9953 | 58.0289 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1274 | 2.8693 | 3.9967
2025-01-01 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.5 | 1 |  | 59.25 | 0.5296 | 26.48 | 26.48 | 0 | 0 | 0 | 26.48 | 32.77 | 9.3629 | 0 | 34.9953 | 34.995 | 34.9953 | 34.9953 | 34.995 | 34.995 | 58.0252 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1235 | 2.8693 | 3.9929
2025-01-01 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.43 | 1 |  | 59.15 | 0.5298 | 26.4912 | 26.4912 | 0 | 0 | 0 | 26.4912 | 32.6588 | 9.3311 | 0 | 34.995 | 34.9947 | 34.995 | 34.995 | 34.9947 | 34.9947 | 58.0216 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1197 | 2.8693 | 3.9891
2025-01-01 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.36 | 1 |  | 59.04 | 0.53 | 26.5024 | 26.5024 | 0 | 0 | 0 | 26.5024 | 32.5376 | 9.2965 | 0 | 34.9947 | 34.9944 | 34.9947 | 34.9947 | 34.9944 | 34.9944 | 58.018 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1156 | 2.8693 | 3.9849
2025-01-01 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.29 | 1 |  | 58.93 | 0.5303 | 26.5136 | 26.5136 | 0 | 0 | 0 | 26.5136 | 32.4164 | 9.2618 | 0 | 34.9944 | 34.9941 | 34.9944 | 34.9944 | 34.9941 | 34.9941 | 58.0143 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1114 | 2.8693 | 3.9808
2025-01-01 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.2 | 1 |  | 58.81 | 0.5306 | 26.528 | 26.528 | 0 | 0 | 0 | 26.528 | 32.282 | 9.2234 | 0 | 34.9941 | 34.9937 | 34.9941 | 34.9941 | 34.9937 | 34.9937 | 58.0107 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1068 | 2.8693 | 3.9762
2025-01-01 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.12 | 1 |  | 58.68 | 0.5308 | 26.5408 | 26.5408 | 0 | 0 | 0 | 26.5408 | 32.1392 | 9.1826 | 0 | 34.9937 | 34.9934 | 34.9937 | 34.9937 | 34.9934 | 34.9934 | 58.0071 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1019 | 2.8693 | 3.9713
2025-01-01 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.03 | 1 |  | 58.55 | 0.5311 | 26.5552 | 26.5552 | 0 | 0 | 0 | 26.5552 | 31.9948 | 9.1414 | 0 | 34.9934 | 34.9931 | 34.9934 | 34.9934 | 34.9931 | 34.9931 | 58.0035 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.097 | 2.8693 | 3.9663
2025-01-01 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.94 | 1 |  | 58.41 | 0.5314 | 26.5696 | 26.5696 | 0 | 0 | 0 | 26.5696 | 31.8404 | 9.0973 | 0 | 34.9931 | 34.9928 | 34.9931 | 34.9931 | 34.9928 | 34.9928 | 57.9998 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0917 | 2.8693 | 3.961
2025-01-01 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.84 | 1 |  | 58.26 | 0.5317 | 26.5856 | 26.5856 | 0 | 0 | 0 | 26.5856 | 31.6744 | 9.0498 | 0 | 34.9928 | 34.9925 | 34.9928 | 34.9928 | 34.9925 | 34.9925 | 57.9962 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.086 | 2.8693 | 3.9553
2025-01-02 | 1 | seasonal | Long-Term / Seasonal Storage | -8.74 | 1 |  | 58.11 | 0.532 | 26.6016 | 26.6016 | 0 | 0 | 0 | 26.6016 | 31.5084 | 9.0024 | 0 | 34.9925 | 34.9922 | 34.9925 | 34.9925 | 34.9922 | 34.9922 | 57.9926 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0803 | 2.8693 | 3.9496
2025-01-02 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.63 | 1 |  | 57.95 | 0.5324 | 26.6192 | 26.6192 | 0 | 0 | 0 | 26.6192 | 31.3308 | 8.9517 | 0 | 34.9922 | 34.9919 | 34.9922 | 34.9922 | 34.9919 | 34.9919 | 57.989 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0742 | 2.8693 | 3.9435
2025-01-02 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.52 | 1 |  | 57.78 | 0.5327 | 26.6368 | 26.6368 | 0 | 0 | 0 | 26.6368 | 31.1432 | 8.8981 | 0 | 34.9919 | 34.9916 | 34.9919 | 34.9919 | 34.9916 | 34.9916 | 57.9853 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0678 | 2.8693 | 3.9371
2025-01-02 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.41 | 1 |  | 57.61 | 0.5331 | 26.6544 | 26.6544 | 0 | 0 | 0 | 26.6544 | 30.9556 | 8.8445 | 0 | 34.9916 | 34.9913 | 34.9916 | 34.9916 | 34.9913 | 34.9913 | 57.9817 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0613 | 2.8693 | 3.9307
2025-01-02 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.29 | 1 |  | 57.44 | 0.5335 | 26.6736 | 26.6736 | 0 | 0 | 0 | 26.6736 | 30.7664 | 8.7904 | 0 | 34.9913 | 34.9909 | 34.9913 | 34.9913 | 34.9909 | 34.9909 | 57.9781 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0548 | 2.8693 | 3.9242
2025-01-02 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.17 | 1 |  | 57.25 | 0.5339 | 26.6928 | 26.6928 | 0 | 0 | 0 | 26.6928 | 30.5572 | 8.7306 | 0 | 34.9909 | 34.9906 | 34.9909 | 34.9909 | 34.9906 | 34.9906 | 57.9744 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0477 | 2.8693 | 3.917
2025-01-02 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.04 | 1 |  | 57.07 | 0.5343 | 26.7136 | 26.7136 | 0 | 0 | 0 | 26.7136 | 30.3564 | 8.6733 | 0 | 34.9906 | 34.9903 | 34.9906 | 34.9906 | 34.9903 | 34.9903 | 57.9708 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0408 | 2.8693 | 3.9101
2025-01-02 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.91 | 1 |  | 56.87 | 0.5347 | 26.7344 | 26.7344 | 0 | 0 | 0 | 26.7344 | 30.1356 | 8.6102 | 0 | 34.9903 | 34.99 | 34.9903 | 34.9903 | 34.99 | 34.99 | 57.9672 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0332 | 2.8693 | 3.9026
2025-01-02 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.78 | 1 |  | 56.67 | 0.5351 | 26.7552 | 26.7552 | 0 | 0 | 0 | 26.7552 | 29.9148 | 8.5471 | 0 | 34.99 | 34.9897 | 34.99 | 34.99 | 34.9897 | 34.9897 | 57.9636 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0257 | 2.8693 | 3.895
2025-01-02 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.64 | 1 |  | 56.47 | 0.5356 | 26.7776 | 26.7776 | 0 | 0 | 0 | 26.7776 | 29.6924 | 8.4835 | 0 | 34.9897 | 34.9894 | 34.9897 | 34.9897 | 34.9894 | 34.9894 | 57.9599 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.018 | 2.8693 | 3.8874
2025-01-02 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.5 | 1 |  | 56.26 | 0.536 | 26.8 | 26.8 | 0 | 0 | 0 | 26.8 | 29.46 | 8.4171 | 0 | 34.9894 | 34.9891 | 34.9894 | 34.9894 | 34.9891 | 34.9891 | 57.9563 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0101 | 2.8693 | 3.8794
2025-01-02 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.36 | 1 |  | 56.04 | 0.5364 | 26.8224 | 26.8224 | 0 | 0 | 0 | 26.8224 | 29.2176 | 8.3479 | 0 | 34.9891 | 34.9888 | 34.9891 | 34.9891 | 34.9888 | 34.9888 | 57.9527 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0017 | 2.8693 | 3.8711
2025-01-02 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.21 | 1 |  | 55.82 | 0.5369 | 26.8464 | 26.8464 | 0 | 0 | 0 | 26.8464 | 28.9736 | 8.2782 | 0 | 34.9888 | 34.9884 | 34.9888 | 34.9888 | 34.9884 | 34.9884 | 57.9491 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9934 | 2.8693 | 3.8627
2025-01-02 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.06 | 1 |  | 55.59 | 0.5374 | 26.8704 | 26.8704 | 0 | 0 | 0 | 26.8704 | 28.7196 | 8.2056 | 0 | 34.9884 | 34.9881 | 34.9884 | 34.9884 | 34.9881 | 34.9881 | 57.9454 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9847 | 2.8693 | 3.854
2025-01-02 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.9 | 1 |  | 55.36 | 0.5379 | 26.896 | 26.896 | 0 | 0 | 0 | 26.896 | 28.464 | 8.1326 | 0 | 34.9881 | 34.9878 | 34.9881 | 34.9881 | 34.9878 | 34.9878 | 57.9418 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9759 | 2.8693 | 3.8453
2025-01-02 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.74 | 1 |  | 55.12 | 0.5384 | 26.9216 | 26.9216 | 0 | 0 | 0 | 26.9216 | 28.1984 | 8.0567 | 0 | 34.9878 | 34.9875 | 34.9878 | 34.9878 | 34.9875 | 34.9875 | 57.9382 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9668 | 2.8693 | 3.8362
2025-01-02 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.58 | 1 |  | 54.87 | 0.5389 | 26.9472 | 26.9472 | 0 | 0 | 0 | 26.9472 | 27.9228 | 7.9779 | 0 | 34.9875 | 34.9872 | 34.9875 | 34.9875 | 34.9872 | 34.9872 | 57.9346 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9574 | 2.8693 | 3.8267
2025-01-02 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.42 | 1 |  | 54.62 | 0.5395 | 26.9728 | 26.9728 | 0 | 0 | 0 | 26.9728 | 27.6472 | 7.8992 | 0 | 34.9872 | 34.9869 | 34.9872 | 34.9872 | 34.9869 | 34.9869 | 57.931 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9479 | 2.8693 | 3.8173
2025-01-02 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.25 | 1 |  | 54.37 | 0.54 | 27 | 27 | 0 | 0 | 0 | 27 | 27.37 | 7.82 | 0 | 34.9869 | 34.9866 | 34.9869 | 34.9869 | 34.9866 | 34.9866 | 57.9273 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9384 | 2.8693 | 3.8077
2025-01-02 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.07 | 1 |  | 54.11 | 0.5406 | 27.0288 | 27.0288 | 0 | 0 | 0 | 27.0288 | 27.0812 | 7.7375 | 0 | 34.9866 | 34.9863 | 34.9866 | 34.9866 | 34.9863 | 34.9863 | 57.9237 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9285 | 2.8693 | 3.7978
2025-01-02 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.9 | 1 |  | 53.85 | 0.5411 | 27.056 | 27.056 | 0 | 0 | 0 | 27.056 | 26.794 | 7.6554 | 0 | 34.9863 | 34.9859 | 34.9863 | 34.9863 | 34.9859 | 34.9859 | 57.9201 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9187 | 2.8693 | 3.788
2025-01-02 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.72 | 1 |  | 53.58 | 0.5417 | 27.0848 | 27.0848 | 0 | 0 | 0 | 27.0848 | 26.4952 | 7.5701 | 0 | 34.9859 | 34.9856 | 34.9859 | 34.9859 | 34.9856 | 34.9856 | 57.9165 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9084 | 2.8693 | 3.7778
2025-01-02 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.54 | 1 |  | 53.31 | 0.5423 | 27.1136 | 27.1136 | 0 | 0 | 0 | 27.1136 | 26.1964 | 7.4847 | 0 | 34.9856 | 34.9853 | 34.9856 | 34.9856 | 34.9853 | 34.9853 | 57.9128 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8982 | 2.8693 | 3.7675
2025-01-02 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.35 | 1 |  | 53.03 | 0.5429 | 27.144 | 27.144 | 0 | 0 | 0 | 27.144 | 25.886 | 7.396 | 0 | 34.9853 | 34.985 | 34.9853 | 34.9853 | 34.985 | 34.985 | 57.9092 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8875 | 2.8693 | 3.7569
2025-01-03 | 1 | seasonal | Long-Term / Seasonal Storage | -5.16 | 1 |  | 52.75 | 0.5435 | 27.1744 | 27.1744 | 0 | 0 | 0 | 27.1744 | 25.5756 | 7.3073 | 0 | 34.985 | 34.9847 | 34.985 | 34.985 | 34.9847 | 34.9847 | 57.9056 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8769 | 2.8693 | 3.7462
2025-01-03 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.97 | 1 |  | 52.46 | 0.5441 | 27.2048 | 27.2048 | 0 | 0 | 0 | 27.2048 | 25.2552 | 7.2158 | 0 | 34.9847 | 34.9844 | 34.9847 | 34.9847 | 34.9844 | 34.9844 | 57.902 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8659 | 2.8693 | 3.7352
2025-01-03 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.78 | 1 |  | 52.17 | 0.5447 | 27.2352 | 27.2352 | 0 | 0 | 0 | 27.2352 | 24.9348 | 7.1242 | 0 | 34.9844 | 34.9841 | 34.9844 | 34.9844 | 34.9841 | 34.9841 | 57.8983 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8549 | 2.8693 | 3.7243
2025-01-03 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.58 | 1 |  | 51.87 | 0.5453 | 27.2672 | 27.2672 | 0 | 0 | 0 | 27.2672 | 24.6028 | 7.0294 | 0 | 34.9841 | 34.9838 | 34.9841 | 34.9841 | 34.9838 | 34.9838 | 57.8947 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8435 | 2.8693 | 3.7129
2025-01-03 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.38 | 1 |  | 51.57 | 0.546 | 27.2992 | 27.2992 | 0 | 0 | 0 | 27.2992 | 24.2708 | 6.9345 | 0 | 34.9838 | 34.9835 | 34.9838 | 34.9838 | 34.9835 | 34.9835 | 57.8911 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8321 | 2.8693 | 3.7015
2025-01-03 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.18 | 1 |  | 51.27 | 0.5466 | 27.3312 | 27.3312 | 0 | 0 | 0 | 27.3312 | 23.9388 | 6.8397 | 0 | 34.9835 | 34.9831 | 34.9835 | 34.9835 | 34.9831 | 34.9831 | 57.8875 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8208 | 2.8693 | 3.6901
2025-01-03 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.97 | 1 |  | 50.96 | 0.5473 | 27.3648 | 27.3648 | 0 | 0 | 0 | 27.3648 | 23.5952 | 6.7415 | 0 | 34.9831 | 34.9828 | 34.9831 | 34.9831 | 34.9828 | 34.9828 | 57.8839 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.809 | 2.8693 | 3.6783
2025-01-03 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.76 | 1 |  | 50.65 | 0.548 | 27.3984 | 27.3984 | 0 | 0 | 0 | 27.3984 | 23.2516 | 6.6433 | 0 | 34.9828 | 34.9825 | 34.9828 | 34.9828 | 34.9825 | 34.9825 | 57.8802 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7972 | 2.8693 | 3.6665
2025-01-03 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.55 | 1 |  | 50.33 | 0.5486 | 27.432 | 27.432 | 0 | 0 | 0 | 27.432 | 22.898 | 6.5423 | 0 | 34.9825 | 34.9822 | 34.9825 | 34.9825 | 34.9822 | 34.9822 | 57.8766 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7851 | 2.8693 | 3.6544
2025-01-03 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.34 | 1 |  | 50.01 | 0.5493 | 27.4656 | 27.4656 | 0 | 0 | 0 | 27.4656 | 22.5444 | 6.4413 | 0 | 34.9822 | 34.9819 | 34.9822 | 34.9822 | 34.9819 | 34.9819 | 57.873 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.773 | 2.8693 | 3.6423
2025-01-03 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.12 | 1 |  | 49.69 | 0.55 | 27.5008 | 27.5008 | 0 | 0 | 0 | 27.5008 | 22.1892 | 6.3398 | 0 | 34.9819 | 34.9816 | 34.9819 | 34.9819 | 34.9816 | 34.9816 | 57.8694 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7608 | 2.8693 | 3.6301
2025-01-03 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.91 | 1 |  | 49.36 | 0.5507 | 27.5344 | 27.5344 | 0 | 0 | 0 | 27.5344 | 21.8256 | 6.2359 | 0 | 34.9816 | 34.9813 | 34.9816 | 34.9816 | 34.9813 | 34.9813 | 57.8658 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7483 | 2.8693 | 3.6177
2025-01-03 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.69 | 1 |  | 49.03 | 0.5514 | 27.5696 | 27.5696 | 0 | 0 | 0 | 27.5696 | 21.4604 | 6.1315 | 0 | 34.9813 | 34.981 | 34.9813 | 34.9813 | 34.981 | 34.981 | 57.8621 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7358 | 2.8693 | 3.6051
2025-01-03 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.46 | 1 |  | 48.69 | 0.5521 | 27.6064 | 27.6064 | 0 | 0 | 0 | 27.6064 | 21.0836 | 6.0239 | 0 | 34.981 | 34.9806 | 34.981 | 34.981 | 34.9806 | 34.9806 | 57.8585 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7229 | 2.8693 | 3.5922
2025-01-03 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.24 | 1 |  | 48.36 | 0.5528 | 27.6416 | 27.6416 | 0 | 0 | 0 | 27.6416 | 20.7184 | 5.9195 | 0 | 34.9806 | 34.9803 | 34.9806 | 34.9806 | 34.9803 | 34.9803 | 57.8549 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7103 | 2.8693 | 3.5797
2025-01-03 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.01 | 1 |  | 48.02 | 0.5536 | 27.6784 | 27.6784 | 0 | 0 | 0 | 27.6784 | 20.3416 | 5.8119 | 0 | 34.9803 | 34.98 | 34.9803 | 34.9803 | 34.98 | 34.98 | 57.8513 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6974 | 2.8693 | 3.5668
2025-01-03 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.78 | 1 |  | 47.67 | 0.5543 | 27.7152 | 27.7152 | 0 | 0 | 0 | 27.7152 | 19.9548 | 5.7014 | 0 | 34.98 | 34.9797 | 34.98 | 34.98 | 34.9797 | 34.9797 | 57.8477 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6842 | 2.8693 | 3.5535
2025-01-03 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.55 | 1 |  | 47.32 | 0.555 | 27.752 | 27.752 | 0 | 0 | 0 | 27.752 | 19.568 | 5.5909 | 0 | 34.9797 | 34.9794 | 34.9797 | 34.9797 | 34.9794 | 34.9794 | 57.8441 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6709 | 2.8693 | 3.5403
2025-01-03 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.32 | 1 |  | 46.97 | 0.5558 | 27.7888 | 27.7888 | 0 | 0 | 0 | 27.7888 | 19.1812 | 5.4803 | 0 | 34.9794 | 34.9791 | 34.9794 | 34.9794 | 34.9791 | 34.9791 | 57.8404 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6576 | 2.8693 | 3.527
2025-01-03 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.08 | 1 |  | 46.62 | 0.5565 | 27.8272 | 27.8272 | 0 | 0 | 0 | 27.8272 | 18.7928 | 5.3694 | 0 | 34.9791 | 34.9788 | 34.9791 | 34.9791 | 34.9788 | 34.9788 | 57.8368 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6443 | 2.8693 | 3.5137
2025-01-03 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.84 | 1 |  | 46.27 | 0.5573 | 27.8656 | 27.8656 | 0 | 0 | 0 | 27.8656 | 18.4044 | 5.2584 | 0 | 34.9788 | 34.9785 | 34.9788 | 34.9788 | 34.9785 | 34.9785 | 57.8332 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.631 | 2.8693 | 3.5004
2025-01-03 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.61 | 1 |  | 45.91 | 0.558 | 27.9024 | 27.9024 | 0 | 0 | 0 | 27.9024 | 18.0076 | 5.145 | 0 | 34.9785 | 34.9782 | 34.9785 | 34.9785 | 34.9782 | 34.9782 | 57.8296 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6174 | 2.8693 | 3.4868
2025-01-03 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.37 | 1 |  | 45.55 | 0.5588 | 27.9408 | 27.9408 | 0 | 0 | 0 | 27.9408 | 17.6092 | 5.0312 | 0 | 34.9782 | 34.9778 | 34.9782 | 34.9782 | 34.9778 | 34.9778 | 57.826 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.6037 | 2.8693 | 3.4731
2025-01-03 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.12 | 1 |  | 45.19 | 0.5596 | 27.9808 | 27.9808 | 0 | 0 | 0 | 27.9808 | 17.2092 | 4.9169 | 0 | 34.9778 | 34.9775 | 34.9778 | 34.9778 | 34.9775 | 34.9775 | 57.8224 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.59 | 2.8693 | 3.4594
2025-01-04 | 1 | seasonal | Long-Term / Seasonal Storage | 0.12 | 1 |  | 44.82 | 0.5604 | 28.0192 | 28.0192 | 0 | 0 | 0 | 28.0192 | 16.8008 | 4.8002 | 0 | 34.9775 | 34.9772 | 34.9775 | 34.9775 | 34.9772 | 34.9772 | 57.8187 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.576 | 2.8693 | 3.4454
2025-01-04 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.36 | 1 |  | 44.45 | 0.5612 | 28.0576 | 28.0576 | 0 | 0 | 0 | 28.0576 | 16.3924 | 4.6835 | 0 | 34.9772 | 34.9769 | 34.9772 | 34.9772 | 34.9769 | 34.9769 | 57.8151 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.562 | 2.8693 | 3.4314
2025-01-04 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.61 | 1 |  | 44.08 | 0.562 | 28.0976 | 28.0976 | 0 | 0 | 0 | 28.0976 | 15.9824 | 4.5664 | 0 | 34.9769 | 34.9766 | 34.9769 | 34.9769 | 34.9766 | 34.9766 | 57.8115 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.548 | 2.8693 | 3.4173
2025-01-04 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.86 | 1 |  | 43.71 | 0.5628 | 28.1376 | 28.1376 | 0 | 0 | 0 | 28.1376 | 15.5724 | 4.4493 | 0 | 34.9766 | 34.9763 | 34.9766 | 34.9766 | 34.9763 | 34.9763 | 57.8079 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.5339 | 2.8693 | 3.4033
2025-01-04 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.11 | 1 |  | 43.34 | 0.5636 | 28.1776 | 28.1776 | 0 | 0 | 0 | 28.1776 | 15.1624 | 4.3321 | 0 | 34.9763 | 34.976 | 34.9763 | 34.9763 | 34.976 | 34.976 | 57.8043 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.5199 | 2.8693 | 3.3892
2025-01-04 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.36 | 1 |  | 42.96 | 0.5644 | 28.2176 | 28.2176 | 0 | 0 | 0 | 28.2176 | 14.7424 | 4.2121 | 0 | 34.976 | 34.9757 | 34.976 | 34.976 | 34.9757 | 34.9757 | 57.8007 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.5055 | 2.8693 | 3.3748
2025-01-04 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.61 | 1 |  | 42.59 | 0.5652 | 28.2576 | 28.2576 | 0 | 0 | 0 | 28.2576 | 14.3324 | 4.095 | 0 | 34.9757 | 34.9754 | 34.9757 | 34.9757 | 34.9754 | 34.9754 | 57.797 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4914 | 2.8693 | 3.3607
2025-01-04 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.86 | 1 |  | 42.21 | 0.566 | 28.2976 | 28.2976 | 0 | 0 | 0 | 28.2976 | 13.9124 | 3.975 | 0 | 34.9754 | 34.975 | 34.9754 | 34.9754 | 34.975 | 34.975 | 57.7934 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.477 | 2.8693 | 3.3463
2025-01-04 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.11 | 1 |  | 41.83 | 0.5668 | 28.3376 | 28.3376 | 0 | 0 | 0 | 28.3376 | 13.4924 | 3.855 | 0 | 34.975 | 34.9747 | 34.975 | 34.975 | 34.9747 | 34.9747 | 57.7898 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4626 | 2.8693 | 3.3319
2025-01-04 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.37 | 1 |  | 41.45 | 0.5676 | 28.3792 | 28.3792 | 0 | 0 | 0 | 28.3792 | 13.0708 | 3.7345 | 0 | 34.9747 | 34.9744 | 34.9747 | 34.9747 | 34.9744 | 34.9744 | 57.7862 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4481 | 2.8693 | 3.3175
2025-01-04 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.62 | 1 |  | 41.07 | 0.5684 | 28.4192 | 28.4192 | 0 | 0 | 0 | 28.4192 | 12.6508 | 3.6145 | 0 | 34.9744 | 34.9741 | 34.9744 | 34.9744 | 34.9741 | 34.9741 | 57.7826 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4337 | 2.8693 | 3.3031
2025-01-04 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.88 | 1 |  | 40.68 | 0.5692 | 28.4608 | 28.4608 | 0 | 0 | 0 | 28.4608 | 12.2192 | 3.4912 | 0 | 34.9741 | 34.9738 | 34.9741 | 34.9741 | 34.9738 | 34.9738 | 57.779 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4189 | 2.8693 | 3.2883
2025-01-04 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.13 | 1 |  | 40.3 | 0.57 | 28.5008 | 28.5008 | 0 | 0 | 0 | 28.5008 | 11.7992 | 3.3712 | 0 | 34.9738 | 34.9735 | 34.9738 | 34.9738 | 34.9735 | 34.9735 | 57.7754 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.4045 | 2.8693 | 3.2739
2025-01-04 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.39 | 1 |  | 39.92 | 0.5708 | 28.5424 | 28.5424 | 0 | 0 | 0 | 28.5424 | 11.3776 | 3.2507 | 0 | 34.9735 | 34.9732 | 34.9735 | 34.9735 | 34.9732 | 34.9732 | 57.7717 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3901 | 2.8693 | 3.2594
2025-01-04 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.65 | 1 |  | 39.53 | 0.5717 | 28.584 | 28.584 | 0 | 0 | 0 | 28.584 | 10.946 | 3.1274 | 0 | 34.9732 | 34.9729 | 34.9732 | 34.9732 | 34.9729 | 34.9729 | 57.7681 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3753 | 2.8693 | 3.2446
2025-01-04 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.9 | 1 |  | 39.14 | 0.5725 | 28.624 | 28.624 | 0 | 0 | 0 | 28.624 | 10.516 | 3.0046 | 0 | 34.9729 | 34.9726 | 34.9729 | 34.9729 | 34.9726 | 34.9726 | 57.7645 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3605 | 2.8693 | 3.2299
2025-01-04 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.16 | 1 |  | 38.76 | 0.5733 | 28.6656 | 28.6656 | 0 | 0 | 0 | 28.6656 | 10.0944 | 2.8841 | 0 | 34.9726 | 34.9722 | 34.9726 | 34.9726 | 34.9722 | 34.9722 | 57.7609 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3461 | 2.8693 | 3.2154
2025-01-04 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.42 | 1 |  | 38.37 | 0.5741 | 28.7072 | 28.7072 | 0 | 0 | 0 | 28.7072 | 9.6628 | 2.7608 | 0 | 34.9722 | 34.9719 | 34.9722 | 34.9722 | 34.9719 | 34.9719 | 57.7573 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3313 | 2.8693 | 3.2006
2025-01-04 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.68 | 1 |  | 37.98 | 0.575 | 28.7488 | 28.7488 | 0 | 0 | 0 | 28.7488 | 9.2312 | 2.6375 | 0 | 34.9719 | 34.9716 | 34.9719 | 34.9719 | 34.9716 | 34.9716 | 57.7537 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.3165 | 2.8693 | 3.1858
2025-01-04 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.94 | 1 |  | 37.6 | 0.5758 | 28.7904 | 28.7904 | 0 | 0 | 0 | 28.7904 | 8.8096 | 2.517 | 0 | 34.9716 | 34.9713 | 34.9716 | 34.9716 | 34.9713 | 34.9713 | 57.7501 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.302 | 2.8693 | 3.1714
2025-01-04 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.19 | 1.058 |  | 37.21 | 0.5845 | 30.9184 | 30.9184 | 0 | 0 | 0 | 30.9184 | 6.2916 | 1.7976 | 0 | 34.9713 | 34.971 | 34.9713 | 34.9713 | 34.971 | 34.971 | 57.7465 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.2157 | 2.8693 | 3.0851
2025-01-04 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.45 | 1.136 |  | 36.82 | 0.5945 | 33.768 | 33.768 | 0 | 0 | 0 | 33.768 | 3.052 | 0.872 | 0 | 34.971 | 34.9707 | 34.971 | 34.971 | 34.9707 | 34.9707 | 57.7428 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.1046 | 2.8693 | 2.974
2025-01-04 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.71 | 1.213 |  | 36.44 | 0.6032 | 36.5816 | 36.44 | 0 | 0 | 0 | 36.44 | 0 | 0 | 0 | 34.9707 | 34.9826 | 34.9707 | 34.9707 | 35.1166 | 34.9704 | 57.8808 | 0.1416 | 0 | 0 | 0 | 0.0036 | 0 | 0 | 2.8693 | 2.8693
2025-01-04 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.97 | 1.29 |  | 36.05 | 0.6108 | 39.3952 | 36.05 | 0 | 0 | 0 | 36.05 | 0 | 0 | 0 | 34.9826 | 35.2702 | 35.1166 | 34.9704 | 38.5717 | 34.9701 | 61.2222 | 3.3452 | 0 | 0 | 0 | 0.0038 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 | 1 | seasonal | Long-Term / Seasonal Storage | 6.23 | 1.368 |  | 35.66 | 0.6176 | 42.2448 | 35.66 | 0 | 0 | 0 | 35.66 | 0 | 0 | 0 | 35.2702 | 35.8367 | 38.5717 | 34.9701 | 45.3728 | 34.9698 | 67.8027 | 6.5848 | 0 | 0 | 0 | 0.0042 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.48 | 1.445 |  | 35.28 | 0.6228 | 44.9971 | 35.28 | 0 | 0 | 0 | 35.28 | 0 | 0 | 0 | 35.8367 | 36.6727 | 45.3728 | 34.9698 | 55.3712 | 34.9694 | 77.515 | 9.7171 | 0 | 0 | 0 | 0.0048 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.74 | 1.522 |  | 34.89 | 0.6072 | 46.211 | 34.89 | 0 | 0 | 0 | 34.89 | 0 | 0 | 0 | 36.6727 | 37.6468 | 55.3712 | 34.9694 | 65.369 | 34.9691 | 88.8305 | 11.321 | 0 | 0 | 0 | 0.0056 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7 | 1.599 |  | 34.51 | 0.5932 | 47.425 | 34.51 | 0 | 0 | 0 | 34.51 | 0 | 0 | 0 | 37.6468 | 38.758 | 65.369 | 34.9691 | 75.3662 | 34.9688 | 101.7391 | 12.915 | 0 | 0 | 0 | 0.0064 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.25 | 1.675 |  | 34.12 | 0.5803 | 48.6014 | 34.12 | 0 | 0 | 0 | 34.12 | 0 | 0 | 0 | 38.758 | 40.004 | 75.3662 | 34.9688 | 79.9969 | 34.9685 | 116.2132 | 14.4814 | 0 | 0 | 0 | 0.0073 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.51 | 1.752 |  | 33.74 | 0.5785 | 50.6741 | 33.74 | 0 | 0 | 0 | 33.74 | 0 | 0 | 0 | 40.004 | 41.461 | 79.9969 | 34.9685 | 79.9969 | 34.9682 | 133.139 | 16.9341 | 0 | 0 | 0 | 0.0083 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.76 | 1.828 |  | 33.36 | 0.5848 | 53.4501 | 33.36 | 0 | 0 | 0 | 33.36 | 0 | 0 | 0 | 41.461 | 43.1896 | 79.9969 | 34.9682 | 79.9969 | 34.9679 | 153.2195 | 20.0901 | 0 | 0 | 0 | 0.0096 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.01 | 1.904 |  | 32.98 | 0.5906 | 56.2261 | 32.98 | 0 | 0 | 0 | 32.98 | 0 | 0 | 0 | 43.1896 | 45.1898 | 79.9969 | 34.9679 | 79.9969 | 34.9676 | 176.4546 | 23.2461 | 0 | 0 | 0 | 0.011 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.27 | 1.98 |  | 32.6 | 0.596 | 59.0037 | 32.6 | 0 | 0 | 0 | 32.6 | 0 | 0 | 0 | 45.1898 | 47.4616 | 79.9969 | 34.9676 | 79.9969 | 34.9673 | 202.8456 | 26.4037 | 0 | 0 | 0 | 0.0127 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.52 | 2.055 |  | 32.22 | 0.6009 | 61.7437 | 32.22 | 0 | 0 | 0 | 32.22 | 0 | 0 | 0 | 47.4616 | 50.0018 | 79.9969 | 34.9673 | 79.9969 | 34.967 | 232.3548 | 29.5237 | 0 | 0 | 0 | 0.0145 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.77 | 2.13 |  | 31.85 | 0.6055 | 64.4837 | 31.85 | 0 | 0 | 0 | 31.85 | 0 | 0 | 0 | 50.0018 | 52.8096 | 79.9969 | 34.967 | 79.9969 | 34.9666 | 264.9719 | 32.6337 | 0 | 0 | 0 | 0.0166 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.02 | 2.205 |  | 31.47 | 0.6097 | 67.2237 | 31.47 | 0 | 0 | 0 | 31.47 | 0 | 0 | 0 | 52.8096 | 55.8858 | 79.9969 | 34.9666 | 79.9969 | 34.9663 | 300.7068 | 35.7537 | 0 | 0 | 0 | 0.0188 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.27 | 2.28 |  | 31.1 | 0.6137 | 69.9637 | 31.1 | 0 | 0 | 0 | 31.1 | 0 | 0 | 0 | 55.8858 | 59.2295 | 79.9969 | 34.9663 | 79.9969 | 34.966 | 339.5492 | 38.8637 | 0 | 0 | 0 | 0.0212 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.51 | 2.354 |  | 30.73 | 0.6174 | 72.6661 | 30.73 | 0 | 0 | 0 | 30.73 | 0 | 0 | 0 | 59.2295 | 62.8374 | 79.9969 | 34.966 | 79.9969 | 34.9657 | 381.4615 | 41.9361 | 0 | 0 | 0 | 0.0239 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.76 | 2.427 |  | 30.36 | 0.6208 | 75.3341 | 30.36 | 0 | 0 | 0 | 30.36 | 0 | 0 | 0 | 62.8374 | 66.7066 | 79.9969 | 34.9657 | 79.9969 | 34.9654 | 426.4089 | 44.9741 | 0 | 0 | 0 | 0.0267 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10 | 2.501 |  | 30 | 0.624 | 78.0365 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 66.7066 | 70.8392 | 79.9969 | 34.9654 | 79.9969 | 34.9651 | 474.4157 | 48.0365 | 0 | 0 | 0 | 0.0297 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.24 | 2.573 |  | 29.63 | 0.627 | 80.6669 | 29.63 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 70.8392 | 75.2298 | 79.9969 | 34.9651 | 79.9969 | 34.9648 | 525.4198 | 51.0369 | 0 | 0 | 0 | 0.0329 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.49 | 2.646 |  | 29.27 | 0.6299 | 83.3349 | 29.27 | 0 | 0 | 0 | 29.27 | 0 | 0 | 0 | 75.2298 | 79.8808 | 79.9969 | 34.9648 | 79.9969 | 78.6038 | 579.4484 | 54.0649 | 0 | 0 | 0 | 0.0362 | 0 | 0 | 2.8693 | 2.8693
2025-01-05 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.73 | 2.718 |  | 28.91 | 0.6326 | 85.9653 | 28.91 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 79.8808 | 79.9969 | 79.9969 | 78.6038 | 79.9969 | 79.9969 | 580.797 | 1.3849 | 0 | 0 | 0 | 0.0363 | 55.6704 | 0 | 2.8693 | 2.8693
2025-01-05 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.96 | 2.789 |  | 28.56 | 0.6351 | 88.5581 | 28.56 | 0 | 0 | 0 | 28.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 59.9618 | 0 | 2.8693 | 2.8693
2025-01-05 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.2 | 2.86 |  | 28.2 | 0.6374 | 91.1525 | 28.2 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 62.9162 | 0 | 2.8693 | 2.8693
2025-01-05 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.43 | 2.93 |  | 27.85 | 0.6397 | 93.7093 | 27.85 | 0 | 0 | 0 | 27.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 65.823 | 0 | 2.8693 | 2.8693
2025-01-05 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.67 | 3 |  | 27.5 | 0.6418 | 96.2677 | 27.5 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 68.7314 | 0 | 2.8693 | 2.8693
2025-01-05 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.9 | 3.069 |  | 27.16 | 0.6438 | 98.7885 | 27.16 | 0 | 0 | 0 | 27.16 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 71.5922 | 0 | 2.8693 | 2.8693
2025-01-06 | 1 | seasonal | Long-Term / Seasonal Storage | 12.12 | 3.137 |  | 26.81 | 0.6457 | 101.2717 | 26.81 | 0 | 0 | 0 | 26.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 74.4254 | 0 | 2.8693 | 2.8693
2025-01-06 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.35 | 3.205 |  | 26.47 | 0.6475 | 103.7565 | 26.47 | 0 | 0 | 0 | 26.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 77.2502 | 0 | 2.8693 | 2.8693
2025-01-06 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.57 | 3.272 |  | 26.14 | 0.6492 | 106.2037 | 26.14 | 0 | 0 | 0 | 26.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 80.0274 | 0 | 2.8693 | 2.8693
2025-01-06 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.8 | 3.339 |  | 25.81 | 0.6508 | 108.6525 | 25.81 | 0 | 0 | 0 | 25.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 82.8062 | 0 | 2.8693 | 2.8693
2025-01-06 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.02 | 3.405 |  | 25.48 | 0.6524 | 111.0637 | 25.48 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 85.5474 | 0 | 2.8693 | 2.8693
2025-01-06 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.23 | 3.47 |  | 25.15 | 0.6538 | 113.4373 | 25.15 | 0 | 0 | 0 | 25.15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 88.251 | 0 | 2.8693 | 2.8693
2025-01-06 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.45 | 3.534 |  | 24.83 | 0.6552 | 115.7765 | 24.83 | 0 | 0 | 0 | 24.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 90.9102 | 0 | 2.8693 | 2.8693
2025-01-06 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.66 | 3.598 |  | 24.51 | 0.6566 | 118.1141 | 24.51 | 0 | 0 | 0 | 24.51 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 93.5678 | 0 | 2.8693 | 2.8693
2025-01-06 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.87 | 3.661 |  | 24.2 | 0.6578 | 120.4157 | 24.2 | 0 | 0 | 0 | 24.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 96.1794 | 0 | 2.8693 | 2.8693
2025-01-06 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.08 | 3.723 |  | 23.89 | 0.659 | 122.6813 | 23.89 | 0 | 0 | 0 | 23.89 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 98.755 | 0 | 2.8693 | 2.8693
2025-01-06 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.28 | 3.784 |  | 23.58 | 0.6602 | 124.9093 | 23.58 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 101.293 | 0 | 2.8693 | 2.8693
2025-01-06 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.48 | 3.844 |  | 23.28 | 0.6613 | 127.1013 | 23.28 | 0 | 0 | 0 | 23.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 103.785 | 0 | 2.8693 | 2.8693
2025-01-06 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.68 | 3.904 |  | 22.98 | 0.6624 | 129.2933 | 22.98 | 0 | 0 | 0 | 22.98 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 106.277 | 0 | 2.8693 | 2.8693
2025-01-06 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.88 | 3.963 |  | 22.69 | 0.6634 | 131.4493 | 22.69 | 0 | 0 | 0 | 22.69 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 108.723 | 0 | 2.8693 | 2.8693
2025-01-06 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.07 | 4.021 |  | 22.4 | 0.6644 | 133.5677 | 22.4 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 111.1314 | 0 | 2.8693 | 2.8693
2025-01-06 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.26 | 4.078 |  | 22.11 | 0.6653 | 135.6501 | 22.11 | 0 | 0 | 0 | 22.11 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 113.5038 | 0 | 2.8693 | 2.8693
2025-01-06 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.45 | 4.134 |  | 21.83 | 0.6662 | 137.6965 | 21.83 | 0 | 0 | 0 | 21.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 115.8302 | 0 | 2.8693 | 2.8693
2025-01-06 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.63 | 4.189 |  | 21.56 | 0.667 | 139.7053 | 21.56 | 0 | 0 | 0 | 21.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 118.109 | 0 | 2.8693 | 2.8693
2025-01-06 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.81 | 4.243 |  | 21.28 | 0.6678 | 141.6781 | 21.28 | 0 | 0 | 0 | 21.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 120.3618 | 0 | 2.8693 | 2.8693
2025-01-06 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.99 | 4.296 |  | 21.02 | 0.6686 | 143.6149 | 21.02 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 122.5586 | 0 | 2.8693 | 2.8693
2025-01-06 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.16 | 4.348 |  | 20.76 | 0.6693 | 145.5141 | 20.76 | 0 | 0 | 0 | 20.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 124.7178 | 0 | 2.8693 | 2.8693
2025-01-06 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.33 | 4.4 |  | 20.5 | 0.6701 | 147.4133 | 20.5 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 126.877 | 0 | 2.8693 | 2.8693
2025-01-06 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.5 | 4.45 |  | 20.25 | 0.6707 | 149.2405 | 20.25 | 0 | 0 | 0 | 20.25 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 128.9542 | 0 | 2.8693 | 2.8693
2025-01-06 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.66 | 4.499 |  | 20 | 0.6714 | 151.0301 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 130.9938 | 0 | 2.8693 | 2.8693
2025-01-07 | 1 | seasonal | Long-Term / Seasonal Storage | 16.82 | 4.547 |  | 19.76 | 0.672 | 152.7837 | 19.76 | 0 | 0 | 0 | 19.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 132.9874 | 0 | 2.8693 | 2.8693
2025-01-07 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.98 | 4.595 |  | 19.53 | 0.6726 | 154.5373 | 19.53 | 0 | 0 | 0 | 19.53 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 134.971 | 0 | 2.8693 | 2.8693
2025-01-07 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.14 | 4.641 |  | 19.3 | 0.6732 | 156.2189 | 19.3 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 136.8826 | 0 | 2.8693 | 2.8693
2025-01-07 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.29 | 4.686 |  | 19.07 | 0.6738 | 157.8629 | 19.07 | 0 | 0 | 0 | 19.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 138.7566 | 0 | 2.8693 | 2.8693
2025-01-07 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.43 | 4.729 |  | 18.85 | 0.6743 | 159.4333 | 18.85 | 0 | 0 | 0 | 18.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 140.547 | 0 | 2.8693 | 2.8693
2025-01-07 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.57 | 4.772 |  | 18.64 | 0.6748 | 161.0037 | 18.64 | 0 | 0 | 0 | 18.64 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 142.3274 | 0 | 2.8693 | 2.8693
2025-01-07 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.71 | 4.814 |  | 18.43 | 0.6753 | 162.5381 | 18.43 | 0 | 0 | 0 | 18.43 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 144.0718 | 0 | 2.8693 | 2.8693
2025-01-07 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.85 | 4.854 |  | 18.23 | 0.6757 | 164.0005 | 18.23 | 0 | 0 | 0 | 18.23 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 145.7342 | 0 | 2.8693 | 2.8693
2025-01-07 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.98 | 4.894 |  | 18.03 | 0.6762 | 165.4613 | 18.03 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 147.395 | 0 | 2.8693 | 2.8693
2025-01-07 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.11 | 4.932 |  | 17.84 | 0.6766 | 166.8501 | 17.84 | 0 | 0 | 0 | 17.84 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 148.9738 | 0 | 2.8693 | 2.8693
2025-01-07 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.23 | 4.969 |  | 17.65 | 0.677 | 168.2013 | 17.65 | 0 | 0 | 0 | 17.65 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 150.515 | 0 | 2.8693 | 2.8693
2025-01-07 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.35 | 5.005 |  | 17.47 | 0.6774 | 169.5165 | 17.47 | 0 | 0 | 0 | 17.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 152.0102 | 0 | 2.8693 | 2.8693
2025-01-07 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.47 | 5.04 |  | 17.3 | 0.6778 | 170.7957 | 17.3 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 153.4594 | 0 | 2.8693 | 2.8693
2025-01-07 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.58 | 5.073 |  | 17.13 | 0.6781 | 172.0013 | 17.13 | 0 | 0 | 0 | 17.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 154.835 | 0 | 2.8693 | 2.8693
2025-01-07 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.69 | 5.106 |  | 16.97 | 0.6784 | 173.2069 | 16.97 | 0 | 0 | 0 | 16.97 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 156.2006 | 0 | 2.8693 | 2.8693
2025-01-07 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.79 | 5.137 |  | 16.82 | 0.6788 | 174.3389 | 16.82 | 0 | 0 | 0 | 16.82 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 157.4826 | 0 | 2.8693 | 2.8693
2025-01-07 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.89 | 5.167 |  | 16.67 | 0.6791 | 175.4349 | 16.67 | 0 | 0 | 0 | 16.67 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 158.7286 | 0 | 2.8693 | 2.8693
2025-01-07 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.98 | 5.195 |  | 16.52 | 0.6793 | 176.4573 | 16.52 | 0 | 0 | 0 | 16.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 159.901 | 0 | 2.8693 | 2.8693
2025-01-07 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.08 | 5.223 |  | 16.39 | 0.6796 | 177.4813 | 16.39 | 0 | 0 | 0 | 16.39 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 161.055 | 0 | 2.8693 | 2.8693
2025-01-07 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.16 | 5.249 |  | 16.26 | 0.6799 | 178.4301 | 16.26 | 0 | 0 | 0 | 16.26 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 162.1338 | 0 | 2.8693 | 2.8693
2025-01-07 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.25 | 5.274 |  | 16.13 | 0.6801 | 179.3445 | 16.13 | 0 | 0 | 0 | 16.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 163.1782 | 0 | 2.8693 | 2.8693
2025-01-07 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.32 | 5.297 |  | 16.01 | 0.6803 | 180.1837 | 16.01 | 0 | 0 | 0 | 16.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 164.1374 | 0 | 2.8693 | 2.8693
2025-01-07 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.4 | 5.32 |  | 15.9 | 0.6805 | 181.0245 | 15.9 | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.0882 | 0 | 2.8693 | 2.8693
2025-01-07 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.47 | 5.341 |  | 15.8 | 0.6807 | 181.7917 | 15.8 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.9554 | 0 | 2.8693 | 2.8693
2025-01-08 | 1 | seasonal | Long-Term / Seasonal Storage | 19.54 | 5.361 |  | 15.7 | 0.6809 | 182.5229 | 15.7 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 166.7866 | 0 | 2.8693 | 2.8693
2025-01-08 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.6 | 5.379 |  | 15.6 | 0.6811 | 183.1805 | 15.6 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 167.5442 | 0 | 2.8693 | 2.8693
2025-01-08 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.65 | 5.396 |  | 15.52 | 0.6812 | 183.8005 | 15.52 | 0 | 0 | 0 | 15.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.2442 | 0 | 2.8693 | 2.8693
2025-01-08 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.71 | 5.412 |  | 15.44 | 0.6814 | 184.3861 | 15.44 | 0 | 0 | 0 | 15.44 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.9098 | 0 | 2.8693 | 2.8693
2025-01-08 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.76 | 5.427 |  | 15.37 | 0.6815 | 184.9341 | 15.37 | 0 | 0 | 0 | 15.37 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 169.5278 | 0 | 2.8693 | 2.8693
2025-01-08 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.8 | 5.44 |  | 15.3 | 0.6816 | 185.4085 | 15.3 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.0722 | 0 | 2.8693 | 2.8693
2025-01-08 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.84 | 5.452 |  | 15.24 | 0.6818 | 185.8469 | 15.24 | 0 | 0 | 0 | 15.24 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.5706 | 0 | 2.8693 | 2.8693
2025-01-08 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.88 | 5.463 |  | 15.19 | 0.6819 | 186.2493 | 15.19 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.023 | 0 | 2.8693 | 2.8693
2025-01-08 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.91 | 5.472 |  | 15.14 | 0.6819 | 186.5781 | 15.14 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.4018 | 0 | 2.8693 | 2.8693
2025-01-08 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.93 | 5.48 |  | 15.1 | 0.682 | 186.8693 | 15.1 | 0 | 0 | 0 | 15.1 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.733 | 0 | 2.8693 | 2.8693
2025-01-08 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.96 | 5.487 |  | 15.07 | 0.6821 | 187.1261 | 15.07 | 0 | 0 | 0 | 15.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.0198 | 0 | 2.8693 | 2.8693
2025-01-08 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.97 | 5.492 |  | 15.04 | 0.6821 | 187.3077 | 15.04 | 0 | 0 | 0 | 15.04 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.2314 | 0 | 2.8693 | 2.8693
2025-01-08 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.496 |  | 15.02 | 0.6822 | 187.4549 | 15.02 | 0 | 0 | 0 | 15.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.3986 | 0 | 2.8693 | 2.8693
2025-01-08 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.498 |  | 15.01 | 0.6822 | 187.5269 | 15.01 | 0 | 0 | 0 | 15.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.4806 | 0 | 2.8693 | 2.8693
2025-01-08 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 20 | 5.5 |  | 15 | 0.6822 | 187.6005 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.5642 | 0 | 2.8693 | 2.8693
2025-01-08 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 20 | 5.5 |  | 15 | 0.6822 | 187.6005 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.5642 | 0 | 2.8693 | 2.8693
2025-01-08 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.498 |  | 15.01 | 0.6822 | 187.5269 | 15.01 | 0 | 0 | 0 | 15.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.4806 | 0 | 2.8693 | 2.8693
2025-01-08 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.99 | 5.496 |  | 15.02 | 0.6822 | 187.4549 | 15.02 | 0 | 0 | 0 | 15.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.3986 | 0 | 2.8693 | 2.8693
2025-01-08 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.97 | 5.492 |  | 15.04 | 0.6821 | 187.3077 | 15.04 | 0 | 0 | 0 | 15.04 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.2314 | 0 | 2.8693 | 2.8693
2025-01-08 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.96 | 5.487 |  | 15.07 | 0.6821 | 187.1261 | 15.07 | 0 | 0 | 0 | 15.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 172.0198 | 0 | 2.8693 | 2.8693
2025-01-08 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.93 | 5.48 |  | 15.1 | 0.682 | 186.8693 | 15.1 | 0 | 0 | 0 | 15.1 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.733 | 0 | 2.8693 | 2.8693
2025-01-08 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.91 | 5.472 |  | 15.14 | 0.6819 | 186.5781 | 15.14 | 0 | 0 | 0 | 15.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.4018 | 0 | 2.8693 | 2.8693
2025-01-08 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.88 | 5.463 |  | 15.19 | 0.6819 | 186.2493 | 15.19 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 171.023 | 0 | 2.8693 | 2.8693
2025-01-08 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.84 | 5.452 |  | 15.24 | 0.6818 | 185.8469 | 15.24 | 0 | 0 | 0 | 15.24 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.5706 | 0 | 2.8693 | 2.8693
2025-01-09 | 1 | seasonal | Long-Term / Seasonal Storage | 19.8 | 5.44 |  | 15.3 | 0.6816 | 185.4085 | 15.3 | 0 | 0 | 0 | 15.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 170.0722 | 0 | 2.8693 | 2.8693
2025-01-09 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.76 | 5.427 |  | 15.37 | 0.6815 | 184.9341 | 15.37 | 0 | 0 | 0 | 15.37 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 169.5278 | 0 | 2.8693 | 2.8693
2025-01-09 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.71 | 5.412 |  | 15.44 | 0.6814 | 184.3861 | 15.44 | 0 | 0 | 0 | 15.44 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.9098 | 0 | 2.8693 | 2.8693
2025-01-09 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.65 | 5.396 |  | 15.52 | 0.6812 | 183.8005 | 15.52 | 0 | 0 | 0 | 15.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 168.2442 | 0 | 2.8693 | 2.8693
2025-01-09 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.6 | 5.379 |  | 15.6 | 0.6811 | 183.1805 | 15.6 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 167.5442 | 0 | 2.8693 | 2.8693
2025-01-09 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.54 | 5.361 |  | 15.7 | 0.6809 | 182.5229 | 15.7 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 166.7866 | 0 | 2.8693 | 2.8693
2025-01-09 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.47 | 5.341 |  | 15.8 | 0.6807 | 181.7917 | 15.8 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.9554 | 0 | 2.8693 | 2.8693
2025-01-09 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.4 | 5.32 |  | 15.9 | 0.6805 | 181.0245 | 15.9 | 0 | 0 | 0 | 15.9 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 165.0882 | 0 | 2.8693 | 2.8693
2025-01-09 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.32 | 5.297 |  | 16.01 | 0.6803 | 180.1837 | 16.01 | 0 | 0 | 0 | 16.01 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 164.1374 | 0 | 2.8693 | 2.8693
2025-01-09 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.25 | 5.274 |  | 16.13 | 0.6801 | 179.3445 | 16.13 | 0 | 0 | 0 | 16.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 163.1782 | 0 | 2.8693 | 2.8693
2025-01-09 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.16 | 5.249 |  | 16.26 | 0.6799 | 178.4301 | 16.26 | 0 | 0 | 0 | 16.26 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 162.1338 | 0 | 2.8693 | 2.8693
2025-01-09 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 19.08 | 5.223 |  | 16.39 | 0.6796 | 177.4813 | 16.39 | 0 | 0 | 0 | 16.39 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 161.055 | 0 | 2.8693 | 2.8693
2025-01-09 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.98 | 5.195 |  | 16.52 | 0.6793 | 176.4573 | 16.52 | 0 | 0 | 0 | 16.52 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 159.901 | 0 | 2.8693 | 2.8693
2025-01-09 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.89 | 5.167 |  | 16.67 | 0.6791 | 175.4349 | 16.67 | 0 | 0 | 0 | 16.67 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 158.7286 | 0 | 2.8693 | 2.8693
2025-01-09 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.79 | 5.137 |  | 16.82 | 0.6788 | 174.3389 | 16.82 | 0 | 0 | 0 | 16.82 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 157.4826 | 0 | 2.8693 | 2.8693
2025-01-09 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.69 | 5.106 |  | 16.97 | 0.6784 | 173.2069 | 16.97 | 0 | 0 | 0 | 16.97 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 156.2006 | 0 | 2.8693 | 2.8693
2025-01-09 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.58 | 5.073 |  | 17.13 | 0.6781 | 172.0013 | 17.13 | 0 | 0 | 0 | 17.13 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 154.835 | 0 | 2.8693 | 2.8693
2025-01-09 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.47 | 5.04 |  | 17.3 | 0.6778 | 170.7957 | 17.3 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 153.4594 | 0 | 2.8693 | 2.8693
2025-01-09 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.35 | 5.005 |  | 17.47 | 0.6774 | 169.5165 | 17.47 | 0 | 0 | 0 | 17.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 152.0102 | 0 | 2.8693 | 2.8693
2025-01-09 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.23 | 4.969 |  | 17.65 | 0.677 | 168.2013 | 17.65 | 0 | 0 | 0 | 17.65 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 150.515 | 0 | 2.8693 | 2.8693
2025-01-09 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 18.11 | 4.932 |  | 17.84 | 0.6766 | 166.8501 | 17.84 | 0 | 0 | 0 | 17.84 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 148.9738 | 0 | 2.8693 | 2.8693
2025-01-09 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.98 | 4.894 |  | 18.03 | 0.6762 | 165.4613 | 18.03 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 147.395 | 0 | 2.8693 | 2.8693
2025-01-09 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.85 | 4.854 |  | 18.23 | 0.6757 | 164.0005 | 18.23 | 0 | 0 | 0 | 18.23 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 145.7342 | 0 | 2.8693 | 2.8693
2025-01-09 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.71 | 4.814 |  | 18.43 | 0.6753 | 162.5381 | 18.43 | 0 | 0 | 0 | 18.43 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 144.0718 | 0 | 2.8693 | 2.8693
2025-01-10 | 1 | seasonal | Long-Term / Seasonal Storage | 17.57 | 4.772 |  | 18.64 | 0.6748 | 161.0037 | 18.64 | 0 | 0 | 0 | 18.64 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 142.3274 | 0 | 2.8693 | 2.8693
2025-01-10 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.43 | 4.729 |  | 18.85 | 0.6743 | 159.4333 | 18.85 | 0 | 0 | 0 | 18.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 140.547 | 0 | 2.8693 | 2.8693
2025-01-10 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.29 | 4.686 |  | 19.07 | 0.6738 | 157.8629 | 19.07 | 0 | 0 | 0 | 19.07 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 138.7566 | 0 | 2.8693 | 2.8693
2025-01-10 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 17.14 | 4.641 |  | 19.3 | 0.6732 | 156.2189 | 19.3 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 136.8826 | 0 | 2.8693 | 2.8693
2025-01-10 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.98 | 4.595 |  | 19.53 | 0.6726 | 154.5373 | 19.53 | 0 | 0 | 0 | 19.53 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 134.971 | 0 | 2.8693 | 2.8693
2025-01-10 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.82 | 4.547 |  | 19.76 | 0.672 | 152.7837 | 19.76 | 0 | 0 | 0 | 19.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 132.9874 | 0 | 2.8693 | 2.8693
2025-01-10 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.66 | 4.499 |  | 20 | 0.6714 | 151.0301 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 130.9938 | 0 | 2.8693 | 2.8693
2025-01-10 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.5 | 4.45 |  | 20.25 | 0.6707 | 149.2405 | 20.25 | 0 | 0 | 0 | 20.25 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 128.9542 | 0 | 2.8693 | 2.8693
2025-01-10 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.33 | 4.4 |  | 20.5 | 0.6701 | 147.4133 | 20.5 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 126.877 | 0 | 2.8693 | 2.8693
2025-01-10 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 16.16 | 4.348 |  | 20.76 | 0.6693 | 145.5141 | 20.76 | 0 | 0 | 0 | 20.76 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 124.7178 | 0 | 2.8693 | 2.8693
2025-01-10 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.99 | 4.296 |  | 21.02 | 0.6686 | 143.6149 | 21.02 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 122.5586 | 0 | 2.8693 | 2.8693
2025-01-10 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.81 | 4.243 |  | 21.28 | 0.6678 | 141.6781 | 21.28 | 0 | 0 | 0 | 21.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 120.3618 | 0 | 2.8693 | 2.8693
2025-01-10 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.63 | 4.189 |  | 21.56 | 0.667 | 139.7053 | 21.56 | 0 | 0 | 0 | 21.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 118.109 | 0 | 2.8693 | 2.8693
2025-01-10 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.45 | 4.134 |  | 21.83 | 0.6662 | 137.6965 | 21.83 | 0 | 0 | 0 | 21.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 115.8302 | 0 | 2.8693 | 2.8693
2025-01-10 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.26 | 4.078 |  | 22.11 | 0.6653 | 135.6501 | 22.11 | 0 | 0 | 0 | 22.11 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 113.5038 | 0 | 2.8693 | 2.8693
2025-01-10 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 15.07 | 4.021 |  | 22.4 | 0.6644 | 133.5677 | 22.4 | 0 | 0 | 0 | 22.4 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 111.1314 | 0 | 2.8693 | 2.8693
2025-01-10 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.88 | 3.963 |  | 22.69 | 0.6634 | 131.4493 | 22.69 | 0 | 0 | 0 | 22.69 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 108.723 | 0 | 2.8693 | 2.8693
2025-01-10 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.68 | 3.904 |  | 22.98 | 0.6624 | 129.2933 | 22.98 | 0 | 0 | 0 | 22.98 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 106.277 | 0 | 2.8693 | 2.8693
2025-01-10 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.48 | 3.844 |  | 23.28 | 0.6613 | 127.1013 | 23.28 | 0 | 0 | 0 | 23.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 103.785 | 0 | 2.8693 | 2.8693
2025-01-10 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.28 | 3.784 |  | 23.58 | 0.6602 | 124.9093 | 23.58 | 0 | 0 | 0 | 23.58 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 101.293 | 0 | 2.8693 | 2.8693
2025-01-10 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 14.08 | 3.723 |  | 23.89 | 0.659 | 122.6813 | 23.89 | 0 | 0 | 0 | 23.89 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 98.755 | 0 | 2.8693 | 2.8693
2025-01-10 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.87 | 3.661 |  | 24.2 | 0.6578 | 120.4157 | 24.2 | 0 | 0 | 0 | 24.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 96.1794 | 0 | 2.8693 | 2.8693
2025-01-10 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.66 | 3.598 |  | 24.51 | 0.6566 | 118.1141 | 24.51 | 0 | 0 | 0 | 24.51 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 93.5678 | 0 | 2.8693 | 2.8693
2025-01-10 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.45 | 3.534 |  | 24.83 | 0.6552 | 115.7765 | 24.83 | 0 | 0 | 0 | 24.83 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 90.9102 | 0 | 2.8693 | 2.8693
2025-01-11 | 1 | seasonal | Long-Term / Seasonal Storage | 13.23 | 3.47 |  | 25.15 | 0.6538 | 113.4373 | 25.15 | 0 | 0 | 0 | 25.15 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 88.251 | 0 | 2.8693 | 2.8693
2025-01-11 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 13.02 | 3.405 |  | 25.48 | 0.6524 | 111.0637 | 25.48 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 85.5474 | 0 | 2.8693 | 2.8693
2025-01-11 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.8 | 3.339 |  | 25.81 | 0.6508 | 108.6525 | 25.81 | 0 | 0 | 0 | 25.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 82.8062 | 0 | 2.8693 | 2.8693
2025-01-11 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.57 | 3.272 |  | 26.14 | 0.6492 | 106.2037 | 26.14 | 0 | 0 | 0 | 26.14 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 80.0274 | 0 | 2.8693 | 2.8693
2025-01-11 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.35 | 3.205 |  | 26.47 | 0.6475 | 103.7565 | 26.47 | 0 | 0 | 0 | 26.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 77.2502 | 0 | 2.8693 | 2.8693
2025-01-11 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 12.12 | 3.137 |  | 26.81 | 0.6457 | 101.2717 | 26.81 | 0 | 0 | 0 | 26.81 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 74.4254 | 0 | 2.8693 | 2.8693
2025-01-11 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.9 | 3.069 |  | 27.16 | 0.6438 | 98.7885 | 27.16 | 0 | 0 | 0 | 27.16 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 71.5922 | 0 | 2.8693 | 2.8693
2025-01-11 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.67 | 3 |  | 27.5 | 0.6418 | 96.2677 | 27.5 | 0 | 0 | 0 | 27.5 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 68.7314 | 0 | 2.8693 | 2.8693
2025-01-11 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.43 | 2.93 |  | 27.85 | 0.6397 | 93.7093 | 27.85 | 0 | 0 | 0 | 27.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 65.823 | 0 | 2.8693 | 2.8693
2025-01-11 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 11.2 | 2.86 |  | 28.2 | 0.6374 | 91.1525 | 28.2 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 62.9162 | 0 | 2.8693 | 2.8693
2025-01-11 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.96 | 2.789 |  | 28.56 | 0.6351 | 88.5581 | 28.56 | 0 | 0 | 0 | 28.56 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 59.9618 | 0 | 2.8693 | 2.8693
2025-01-11 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.73 | 2.718 |  | 28.91 | 0.6326 | 85.9653 | 28.91 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 57.019 | 0 | 2.8693 | 2.8693
2025-01-11 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.49 | 2.646 |  | 29.27 | 0.6299 | 83.3349 | 29.27 | 0 | 0 | 0 | 29.27 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 54.0286 | 0 | 2.8693 | 2.8693
2025-01-11 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10.24 | 2.573 |  | 29.63 | 0.627 | 80.6669 | 29.63 | 0 | 0 | 0 | 29.63 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 51.0006 | 0 | 2.8693 | 2.8693
2025-01-11 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 10 | 2.501 |  | 30 | 0.624 | 78.0365 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 48.0002 | 0 | 2.8693 | 2.8693
2025-01-11 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.76 | 2.427 |  | 30.36 | 0.6208 | 75.3341 | 30.36 | 0 | 0 | 0 | 30.36 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 44.9378 | 0 | 2.8693 | 2.8693
2025-01-11 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.51 | 2.354 |  | 30.73 | 0.6174 | 72.6661 | 30.73 | 0 | 0 | 0 | 30.73 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 41.8998 | 0 | 2.8693 | 2.8693
2025-01-11 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.27 | 2.28 |  | 31.1 | 0.6137 | 69.9637 | 31.1 | 0 | 0 | 0 | 31.1 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 38.8274 | 0 | 2.8693 | 2.8693
2025-01-11 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 9.02 | 2.205 |  | 31.47 | 0.6097 | 67.2237 | 31.47 | 0 | 0 | 0 | 31.47 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 35.7174 | 0 | 2.8693 | 2.8693
2025-01-11 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.77 | 2.13 |  | 31.85 | 0.6055 | 64.4837 | 31.85 | 0 | 0 | 0 | 31.85 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 32.5974 | 0 | 2.8693 | 2.8693
2025-01-11 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.52 | 2.055 |  | 32.22 | 0.6009 | 61.7437 | 32.22 | 0 | 0 | 0 | 32.22 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 29.4874 | 0 | 2.8693 | 2.8693
2025-01-11 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.27 | 1.98 |  | 32.6 | 0.596 | 59.0037 | 32.6 | 0 | 0 | 0 | 32.6 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 26.3674 | 0 | 2.8693 | 2.8693
2025-01-11 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 8.01 | 1.904 |  | 32.98 | 0.5906 | 56.2261 | 32.98 | 0 | 0 | 0 | 32.98 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 23.2098 | 0 | 2.8693 | 2.8693
2025-01-11 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.76 | 1.828 |  | 33.36 | 0.5848 | 53.4501 | 33.36 | 0 | 0 | 0 | 33.36 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 20.0538 | 0 | 2.8693 | 2.8693
2025-01-12 | 1 | seasonal | Long-Term / Seasonal Storage | 7.51 | 1.752 |  | 33.74 | 0.5785 | 50.6741 | 33.74 | 0 | 0 | 0 | 33.74 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 16.8978 | 0 | 2.8693 | 2.8693
2025-01-12 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7.25 | 1.675 |  | 34.12 | 0.5715 | 47.8605 | 34.12 | 0 | 0 | 0 | 34.12 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 13.7042 | 0 | 2.8693 | 2.8693
2025-01-12 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 7 | 1.599 |  | 34.51 | 0.5639 | 45.0845 | 34.51 | 0 | 0 | 0 | 34.51 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 10.5382 | 0 | 2.8693 | 2.8693
2025-01-12 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.74 | 1.522 |  | 34.89 | 0.5555 | 42.2709 | 34.89 | 0 | 0 | 0 | 34.89 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 7.3446 | 0 | 2.8693 | 2.8693
2025-01-12 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.48 | 1.445 |  | 35.28 | 0.5461 | 39.4573 | 35.28 | 0 | 0 | 0 | 35.28 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 4.141 | 0 | 2.8693 | 2.8693
2025-01-12 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 6.23 | 1.368 |  | 35.66 | 0.5358 | 36.6453 | 35.66 | 0 | 0 | 0 | 35.66 | 0 | 0 | 0 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 79.9969 | 580.797 | 0.0363 | 0 | 0 | 0 | 0.0363 | 0.949 | 0 | 2.8693 | 2.8693
2025-01-12 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.97 | 1.29 |  | 36.05 | 0.524 | 33.7957 | 33.7957 | 2.2543 | 0 | 0 | 36.05 | 0 | 0 | 0 | 79.9969 | 79.7997 | 79.9969 | 79.9969 | 79.9937 | 77.6652 | 578.5065 | 0 | 2.2543 | 0 | 2.2543 | 0.0362 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.71 | 1.213 |  | 36.44 | 0.5108 | 30.9826 | 30.9826 | 5.4574 | 0 | 0 | 36.44 | 0 | 0 | 0 | 79.7997 | 79.3268 | 79.9937 | 77.6652 | 79.9906 | 74.3535 | 573.0133 | 0 | 5.4574 | 0 | 5.4574 | 0.0358 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.45 | 1.136 |  | 36.82 | 0.4959 | 28.1695 | 28.1695 | 8.6505 | 0 | 0 | 36.82 | 0 | 0 | 0 | 79.3268 | 78.5791 | 79.9906 | 74.3535 | 79.9875 | 71.0521 | 564.3275 | 0 | 8.6505 | 0 | 8.6505 | 0.0353 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | 5.19 | 1.058 |  | 37.21 | 0.4786 | 25.3204 | 25.3204 | 11.8896 | 0 | 0 | 37.21 | 0 | 0 | 0 | 78.5791 | 77.5527 | 79.9875 | 71.0521 | 79.9844 | 67.7032 | 552.4033 | 0 | 11.8896 | 0 | 11.8896 | 0.0346 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.94 | 1 |  | 37.6 | 0.4639 | 23.1929 | 23.1929 | 14.4071 | 0 | 0 | 37.6 | 0 | 0 | 0 | 77.5527 | 76.3095 | 79.9844 | 67.7032 | 79.9812 | 65.0997 | 537.9626 | 0 | 14.4071 | 0 | 14.4071 | 0.0336 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.68 | 1 |  | 37.98 | 0.463 | 23.1518 | 23.1518 | 14.8282 | 0 | 0 | 37.98 | 0 | 0 | 0 | 76.3095 | 75.0303 | 79.9812 | 65.0997 | 79.9781 | 64.6616 | 523.1017 | 0 | 14.8282 | 0 | 14.8282 | 0.0327 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.42 | 1 |  | 38.37 | 0.4622 | 23.1107 | 23.1107 | 15.2593 | 0 | 0 | 38.37 | 0 | 0 | 0 | 75.0303 | 73.714 | 79.9781 | 64.6616 | 79.975 | 64.2131 | 507.8106 | 0 | 15.2593 | 0 | 15.2593 | 0.0318 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | 4.16 | 1 |  | 38.76 | 0.4614 | 23.0696 | 23.0696 | 15.6904 | 0 | 0 | 38.76 | 0 | 0 | 0 | 73.714 | 72.3606 | 79.975 | 64.2131 | 79.9719 | 63.7647 | 492.0894 | 0 | 15.6904 | 0 | 15.6904 | 0.0308 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.9 | 1 |  | 39.14 | 0.4606 | 23.0285 | 23.0285 | 16.1115 | 0 | 0 | 39.14 | 0 | 0 | 0 | 72.3606 | 70.9711 | 79.9719 | 63.7647 | 79.9687 | 63.3266 | 475.9482 | 0 | 16.1115 | 0 | 16.1115 | 0.0298 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.65 | 1 |  | 39.53 | 0.4598 | 22.989 | 22.989 | 16.541 | 0 | 0 | 39.53 | 0 | 0 | 0 | 70.9711 | 69.5448 | 79.9687 | 63.3266 | 79.9656 | 62.8799 | 459.3784 | 0 | 16.541 | 0 | 16.541 | 0.0287 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.39 | 1 |  | 39.92 | 0.459 | 22.9479 | 22.9479 | 16.9721 | 0 | 0 | 39.92 | 0 | 0 | 0 | 69.5448 | 68.0814 | 79.9656 | 62.8799 | 79.9625 | 62.4314 | 442.3787 | 0 | 16.9721 | 0 | 16.9721 | 0.0277 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | 3.13 | 1 |  | 40.3 | 0.4581 | 22.9068 | 22.9068 | 17.3932 | 0 | 0 | 40.3 | 0 | 0 | 0 | 68.0814 | 66.5818 | 79.9625 | 62.4314 | 77.6324 | 61.9933 | 424.9589 | 0 | 17.3932 | 0 | 17.3932 | 0.0266 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.88 | 1 |  | 40.68 | 0.4648 | 23.2396 | 23.2396 | 17.4404 | 0 | 0 | 40.68 | 0 | 0 | 0 | 66.5818 | 65.0783 | 77.6324 | 61.9933 | 74.323 | 59.6147 | 407.493 | 0 | 17.4404 | 0 | 17.4404 | 0.0255 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.62 | 1 |  | 41.07 | 0.4746 | 23.7275 | 23.7275 | 17.3425 | 0 | 0 | 41.07 | 0 | 0 | 0 | 65.0783 | 63.5833 | 74.323 | 59.6147 | 71.0239 | 56.4066 | 390.1261 | 0 | 17.3425 | 0 | 17.3425 | 0.0244 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.37 | 1 |  | 41.45 | 0.4843 | 24.2154 | 24.2154 | 17.2346 | 0 | 0 | 41.45 | 0 | 0 | 0 | 63.5833 | 62.0977 | 71.0239 | 56.4066 | 67.6773 | 53.2191 | 372.8682 | 0 | 17.2346 | 0 | 17.2346 | 0.0233 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | 2.11 | 1 |  | 41.83 | 0.4942 | 24.7092 | 24.7092 | 17.1208 | 0 | 0 | 41.83 | 0 | 0 | 0 | 62.0977 | 60.622 | 67.6773 | 53.2191 | 65.0755 | 49.9903 | 355.7252 | 0 | 17.1208 | 0 | 17.1208 | 0.0223 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.86 | 1 |  | 42.21 | 0.5017 | 25.0855 | 25.0855 | 17.1245 | 0 | 0 | 42.21 | 0 | 0 | 0 | 60.622 | 59.146 | 65.0755 | 49.9903 | 64.6377 | 47.3849 | 338.5795 | 0 | 17.1245 | 0 | 17.1245 | 0.0212 | 0 | 0 | 2.8693 | 2.8693
2025-01-12 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.61 | 1 |  | 42.59 | 0.5023 | 25.1156 | 25.1156 | 17.4744 | 0 | 0 | 42.59 | 0 | 0 | 0 | 59.146 | 57.64 | 64.6377 | 47.3849 | 64.1896 | 46.5856 | 321.085 | 0 | 17.4744 | 0 | 17.4744 | 0.0201 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 | 1 | seasonal | Long-Term / Seasonal Storage | 1.36 | 1 |  | 42.96 | 0.5029 | 25.1473 | 25.1473 | 17.8127 | 0 | 0 | 42.96 | 0 | 0 | 0 | 57.64 | 56.105 | 64.1896 | 46.5856 | 63.7415 | 45.7881 | 303.2533 | 0 | 17.8127 | 0 | 17.8127 | 0.019 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | 1.11 | 1 |  | 43.34 | 0.5036 | 25.179 | 25.179 | 18.161 | 0 | 0 | 43.34 | 0 | 0 | 0 | 56.105 | 54.5401 | 63.7415 | 45.7881 | 63.2849 | 44.9991 | 285.0744 | 0 | 18.161 | 0 | 18.161 | 0.0178 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.86 | 1 |  | 43.71 | 0.5042 | 25.212 | 25.212 | 18.498 | 0 | 0 | 43.71 | 0 | 0 | 0 | 54.5401 | 52.9463 | 63.2849 | 44.9991 | 62.4112 | 44.9981 | 266.5598 | 0 | 18.498 | 0 | 18.498 | 0.0167 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.61 | 1 |  | 44.08 | 0.5062 | 25.3118 | 25.3118 | 18.7682 | 0 | 0 | 44.08 | 0 | 0 | 0 | 52.9463 | 51.3294 | 62.4112 | 44.9981 | 61.9733 | 44.9972 | 247.7761 | 0 | 18.7682 | 0 | 18.7682 | 0.0155 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.36 | 1 |  | 44.45 | 0.5068 | 25.3419 | 25.3419 | 19.1081 | 0 | 0 | 44.45 | 0 | 0 | 0 | 51.3294 | 49.6832 | 61.9733 | 44.9972 | 59.5962 | 44.9962 | 228.6536 | 0 | 19.1081 | 0 | 19.1081 | 0.0143 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | 0.12 | 1 |  | 44.82 | 0.5137 | 25.6838 | 25.6838 | 19.1362 | 0 | 0 | 44.82 | 0 | 0 | 0 | 49.6832 | 48.0348 | 59.5962 | 44.9962 | 56.3901 | 44.9953 | 209.5044 | 0 | 19.1362 | 0 | 19.1362 | 0.0131 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.12 | 1 |  | 45.19 | 0.5232 | 26.1584 | 26.1584 | 19.0316 | 0 | 0 | 45.19 | 0 | 0 | 0 | 48.0348 | 46.3955 | 56.3901 | 44.9953 | 52.0507 | 44.9944 | 190.4608 | 0 | 19.0316 | 0 | 19.0316 | 0.0119 | 0 | 0 | 2.8693 | 2.8693
2025-01-13 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.37 | 1 |  | 45.55 | 0.5363 | 26.8127 | 26.8127 | 16.2308 | 2.5065 | 1.7904 | 45.55 | 0 | 0.7161 | 0.7161 | 46.3955 | 44.8432 | 52.0507 | 44.9944 | 44.9991 | 43.1497 | 172.4289 | 0 | 16.2308 | 1.7904 | 18.0212 | 0.0108 | 0 | 0.0859 | 2.8693 | 2.9553
2025-01-13 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.61 | 1 |  | 45.91 | 0.558 | 27.9024 | 27.9024 | 0 | 18.0076 | 12.8626 | 45.91 | 0 | 5.145 | 5.145 | 44.8432 | 43.7351 | 44.9991 | 43.1497 | 44.9981 | 34.9997 | 159.5563 | 0 | 0 | 12.8626 | 12.8626 | 0.01 | 0 | 0.6174 | 2.8693 | 3.4868
2025-01-13 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -0.84 | 1 |  | 46.27 | 0.5573 | 27.8656 | 27.8656 | 0 | 18.4044 | 13.146 | 46.27 | 0 | 5.2584 | 5.2584 | 43.7351 | 42.6027 | 44.9981 | 34.9997 | 44.9962 | 34.9994 | 146.4012 | 0 | 0 | 13.146 | 13.146 | 0.0092 | 0 | 0.631 | 2.8693 | 3.5004
2025-01-13 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.08 | 1 |  | 46.62 | 0.5565 | 27.8272 | 27.8272 | 0 | 18.7928 | 13.4234 | 46.62 | 0 | 5.3694 | 5.3694 | 42.6027 | 41.4464 | 44.9962 | 34.9994 | 44.9944 | 34.9991 | 132.9694 | 0 | 0 | 13.4234 | 13.4234 | 0.0083 | 0 | 0.6443 | 2.8693 | 3.5137
2025-01-13 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.32 | 1 |  | 46.97 | 0.5558 | 27.7888 | 27.7888 | 0 | 19.1812 | 13.7009 | 46.97 | 0 | 5.4803 | 5.4803 | 41.4464 | 40.2664 | 44.9944 | 34.9991 | 44.9916 | 34.9987 | 119.2611 | 0 | 0 | 13.7009 | 13.7009 | 0.0075 | 0 | 0.6576 | 2.8693 | 3.527
2025-01-13 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.55 | 1 |  | 47.32 | 0.555 | 27.752 | 27.752 | 0 | 19.568 | 13.9771 | 47.32 | 0 | 5.5909 | 5.5909 | 40.2664 | 39.0626 | 44.9916 | 34.9987 | 44.9887 | 34.9984 | 105.2774 | 0 | 0 | 13.9771 | 13.9771 | 0.0066 | 0 | 0.6709 | 2.8693 | 3.5403
2025-01-13 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -1.78 | 1 |  | 47.67 | 0.5543 | 27.7152 | 27.7152 | 0 | 19.9548 | 14.2534 | 47.67 | 0 | 5.7014 | 5.7014 | 39.0626 | 37.8351 | 44.9887 | 34.9984 | 41.7067 | 34.9981 | 91.0183 | 0 | 0 | 14.2534 | 14.2534 | 0.0057 | 0 | 0.6842 | 2.8693 | 3.5535
2025-01-13 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.01 | 1 |  | 48.02 | 0.5536 | 27.6784 | 27.6784 | 0 | 20.3416 | 14.5297 | 48.02 | 0 | 5.8119 | 5.8119 | 37.8351 | 36.584 | 41.7067 | 34.9981 | 40.8321 | 34.9978 | 76.4838 | 0 | 0 | 14.5297 | 14.5297 | 0.0048 | 0 | 0.6974 | 2.8693 | 3.5668
2025-01-13 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.24 | 1 |  | 48.36 | 0.5528 | 27.6416 | 27.6416 | 0 | 20.7184 | 14.7989 | 48.36 | 0 | 5.9195 | 5.9195 | 36.584 | 35.3097 | 40.8321 | 34.9978 | 38.409 | 34.9975 | 61.6811 | 0 | 0 | 14.7989 | 14.7989 | 0.0039 | 0 | 0.7103 | 2.8693 | 3.5797
2025-01-13 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.46 | 1 |  | 48.69 | 0.5521 | 27.6064 | 27.6064 | 0 | 5.0533 | 3.6095 | 32.6597 | 16.0303 | 6.0239 | 1.4438 | 35.3097 | 34.9987 | 38.409 | 34.9975 | 34.9997 | 34.9972 | 58.0679 | 0 | 0 | 3.6095 | 3.6095 | 0.0036 | 0 | 0.7229 | 2.8693 | 3.5922
2025-01-13 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.69 | 1 |  | 49.03 | 0.5514 | 27.5696 | 27.5696 | 0 | 0 | 0 | 27.5696 | 21.4604 | 6.1315 | 0 | 34.9987 | 34.9984 | 34.9997 | 34.9972 | 34.9994 | 34.9969 | 58.0643 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7358 | 2.8693 | 3.6051
2025-01-13 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -2.91 | 1 |  | 49.36 | 0.5507 | 27.5344 | 27.5344 | 0 | 0 | 0 | 27.5344 | 21.8256 | 6.2359 | 0 | 34.9984 | 34.998 | 34.9994 | 34.9969 | 34.9991 | 34.9966 | 58.0606 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7483 | 2.8693 | 3.6177
2025-01-13 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.12 | 1 |  | 49.69 | 0.55 | 27.5008 | 27.5008 | 0 | 0 | 0 | 27.5008 | 22.1892 | 6.3398 | 0 | 34.998 | 34.9977 | 34.9991 | 34.9966 | 34.9987 | 34.9962 | 58.057 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7608 | 2.8693 | 3.6301
2025-01-13 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.34 | 1 |  | 50.01 | 0.5493 | 27.4656 | 27.4656 | 0 | 0 | 0 | 27.4656 | 22.5444 | 6.4413 | 0 | 34.9977 | 34.9974 | 34.9987 | 34.9962 | 34.9984 | 34.9959 | 58.0534 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.773 | 2.8693 | 3.6423
2025-01-13 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.55 | 1 |  | 50.33 | 0.5486 | 27.432 | 27.432 | 0 | 0 | 0 | 27.432 | 22.898 | 6.5423 | 0 | 34.9974 | 34.9971 | 34.9984 | 34.9959 | 34.9981 | 34.9956 | 58.0497 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7851 | 2.8693 | 3.6544
2025-01-13 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.76 | 1 |  | 50.65 | 0.548 | 27.3984 | 27.3984 | 0 | 0 | 0 | 27.3984 | 23.2516 | 6.6433 | 0 | 34.9971 | 34.9968 | 34.9981 | 34.9956 | 34.9978 | 34.9953 | 58.0461 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.7972 | 2.8693 | 3.6665
2025-01-13 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -3.97 | 1 |  | 50.96 | 0.5473 | 27.3648 | 27.3648 | 0 | 0 | 0 | 27.3648 | 23.5952 | 6.7415 | 0 | 34.9968 | 34.9965 | 34.9978 | 34.9953 | 34.9975 | 34.995 | 58.0425 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.809 | 2.8693 | 3.6783
2025-01-14 | 1 | seasonal | Long-Term / Seasonal Storage | -4.18 | 1 |  | 51.27 | 0.5466 | 27.3312 | 27.3312 | 0 | 0 | 0 | 27.3312 | 23.9388 | 6.8397 | 0 | 34.9965 | 34.9962 | 34.9975 | 34.995 | 34.9972 | 34.9947 | 58.0388 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8208 | 2.8693 | 3.6901
2025-01-14 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.38 | 1 |  | 51.57 | 0.546 | 27.2992 | 27.2992 | 0 | 0 | 0 | 27.2992 | 24.2708 | 6.9345 | 0 | 34.9962 | 34.9959 | 34.9972 | 34.9947 | 34.9969 | 34.9944 | 58.0352 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8321 | 2.8693 | 3.7015
2025-01-14 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.58 | 1 |  | 51.87 | 0.5453 | 27.2672 | 27.2672 | 0 | 0 | 0 | 27.2672 | 24.6028 | 7.0294 | 0 | 34.9959 | 34.9955 | 34.9969 | 34.9944 | 34.9966 | 34.9941 | 58.0316 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8435 | 2.8693 | 3.7129
2025-01-14 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.78 | 1 |  | 52.17 | 0.5447 | 27.2352 | 27.2352 | 0 | 0 | 0 | 27.2352 | 24.9348 | 7.1242 | 0 | 34.9955 | 34.9952 | 34.9966 | 34.9941 | 34.9962 | 34.9937 | 58.028 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8549 | 2.8693 | 3.7243
2025-01-14 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -4.97 | 1 |  | 52.46 | 0.5441 | 27.2048 | 27.2048 | 0 | 0 | 0 | 27.2048 | 25.2552 | 7.2158 | 0 | 34.9952 | 34.9949 | 34.9962 | 34.9937 | 34.9959 | 34.9934 | 58.0243 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8659 | 2.8693 | 3.7352
2025-01-14 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.16 | 1 |  | 52.75 | 0.5435 | 27.1744 | 27.1744 | 0 | 0 | 0 | 27.1744 | 25.5756 | 7.3073 | 0 | 34.9949 | 34.9946 | 34.9959 | 34.9934 | 34.9956 | 34.9931 | 58.0207 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8769 | 2.8693 | 3.7462
2025-01-14 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.35 | 1 |  | 53.03 | 0.5429 | 27.144 | 27.144 | 0 | 0 | 0 | 27.144 | 25.886 | 7.396 | 0 | 34.9946 | 34.9943 | 34.9956 | 34.9931 | 34.9953 | 34.9928 | 58.0171 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8875 | 2.8693 | 3.7569
2025-01-14 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.54 | 1 |  | 53.31 | 0.5423 | 27.1136 | 27.1136 | 0 | 0 | 0 | 27.1136 | 26.1964 | 7.4847 | 0 | 34.9943 | 34.994 | 34.9953 | 34.9928 | 34.995 | 34.9925 | 58.0134 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.8982 | 2.8693 | 3.7675
2025-01-14 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.72 | 1 |  | 53.58 | 0.5417 | 27.0848 | 27.0848 | 0 | 0 | 0 | 27.0848 | 26.4952 | 7.5701 | 0 | 34.994 | 34.9937 | 34.995 | 34.9925 | 34.9947 | 34.9922 | 58.0098 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9084 | 2.8693 | 3.7778
2025-01-14 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -5.9 | 1 |  | 53.85 | 0.5411 | 27.056 | 27.056 | 0 | 0 | 0 | 27.056 | 26.794 | 7.6554 | 0 | 34.9937 | 34.9934 | 34.9947 | 34.9922 | 34.9944 | 34.9919 | 58.0062 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9187 | 2.8693 | 3.788
2025-01-14 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.07 | 1 |  | 54.11 | 0.5406 | 27.0288 | 27.0288 | 0 | 0 | 0 | 27.0288 | 27.0812 | 7.7375 | 0 | 34.9934 | 34.993 | 34.9944 | 34.9919 | 34.9941 | 34.9916 | 58.0026 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9285 | 2.8693 | 3.7978
2025-01-14 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.25 | 1 |  | 54.37 | 0.54 | 27 | 27 | 0 | 0 | 0 | 27 | 27.37 | 7.82 | 0 | 34.993 | 34.9927 | 34.9941 | 34.9916 | 34.9937 | 34.9913 | 57.9989 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9384 | 2.8693 | 3.8077
2025-01-14 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.42 | 1 |  | 54.62 | 0.5395 | 26.9728 | 26.9728 | 0 | 0 | 0 | 26.9728 | 27.6472 | 7.8992 | 0 | 34.9927 | 34.9924 | 34.9937 | 34.9913 | 34.9934 | 34.9909 | 57.9953 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9479 | 2.8693 | 3.8173
2025-01-14 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.58 | 1 |  | 54.87 | 0.5389 | 26.9472 | 26.9472 | 0 | 0 | 0 | 26.9472 | 27.9228 | 7.9779 | 0 | 34.9924 | 34.9921 | 34.9934 | 34.9909 | 34.9931 | 34.9906 | 57.9917 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9574 | 2.8693 | 3.8267
2025-01-14 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.74 | 1 |  | 55.12 | 0.5384 | 26.9216 | 26.9216 | 0 | 0 | 0 | 26.9216 | 28.1984 | 8.0567 | 0 | 34.9921 | 34.9918 | 34.9931 | 34.9906 | 34.9928 | 34.9903 | 57.988 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9668 | 2.8693 | 3.8362
2025-01-14 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -6.9 | 1 |  | 55.36 | 0.5379 | 26.896 | 26.896 | 0 | 0 | 0 | 26.896 | 28.464 | 8.1326 | 0 | 34.9918 | 34.9915 | 34.9928 | 34.9903 | 34.9925 | 34.99 | 57.9844 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9759 | 2.8693 | 3.8453
2025-01-14 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.06 | 1 |  | 55.59 | 0.5374 | 26.8704 | 26.8704 | 0 | 0 | 0 | 26.8704 | 28.7196 | 8.2056 | 0 | 34.9915 | 34.9912 | 34.9925 | 34.99 | 34.9922 | 34.9897 | 57.9808 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9847 | 2.8693 | 3.854
2025-01-14 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.21 | 1 |  | 55.82 | 0.5369 | 26.8464 | 26.8464 | 0 | 0 | 0 | 26.8464 | 28.9736 | 8.2782 | 0 | 34.9912 | 34.9909 | 34.9922 | 34.9897 | 34.9919 | 34.9894 | 57.9772 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 0.9934 | 2.8693 | 3.8627
2025-01-14 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.36 | 1 |  | 56.04 | 0.5364 | 26.8224 | 26.8224 | 0 | 0 | 0 | 26.8224 | 29.2176 | 8.3479 | 0 | 34.9909 | 34.9905 | 34.9919 | 34.9894 | 34.9916 | 34.9891 | 57.9735 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0017 | 2.8693 | 3.8711
2025-01-14 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.5 | 1 |  | 56.26 | 0.536 | 26.8 | 26.8 | 0 | 0 | 0 | 26.8 | 29.46 | 8.4171 | 0 | 34.9905 | 34.9902 | 34.9916 | 34.9891 | 34.9913 | 34.9888 | 57.9699 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0101 | 2.8693 | 3.8794
2025-01-14 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.64 | 1 |  | 56.47 | 0.5356 | 26.7776 | 26.7776 | 0 | 0 | 0 | 26.7776 | 29.6924 | 8.4835 | 0 | 34.9902 | 34.9899 | 34.9913 | 34.9888 | 34.9909 | 34.9884 | 57.9663 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.018 | 2.8693 | 3.8874
2025-01-14 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.78 | 1 |  | 56.67 | 0.5351 | 26.7552 | 26.7552 | 0 | 0 | 0 | 26.7552 | 29.9148 | 8.5471 | 0 | 34.9899 | 34.9896 | 34.9909 | 34.9884 | 34.9906 | 34.9881 | 57.9627 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0257 | 2.8693 | 3.895
2025-01-14 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -7.91 | 1 |  | 56.87 | 0.5347 | 26.7344 | 26.7344 | 0 | 0 | 0 | 26.7344 | 30.1356 | 8.6102 | 0 | 34.9896 | 34.9893 | 34.9906 | 34.9881 | 34.9903 | 34.9878 | 57.959 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0332 | 2.8693 | 3.9026
2025-01-14 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.04 | 1 |  | 57.07 | 0.5343 | 26.7136 | 26.7136 | 0 | 0 | 0 | 26.7136 | 30.3564 | 8.6733 | 0 | 34.9893 | 34.989 | 34.9903 | 34.9878 | 34.99 | 34.9875 | 57.9554 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0408 | 2.8693 | 3.9101
2025-01-15 | 1 | seasonal | Long-Term / Seasonal Storage | -8.17 | 1 |  | 57.25 | 0.5339 | 26.6928 | 26.6928 | 0 | 0 | 0 | 26.6928 | 30.5572 | 8.7306 | 0 | 34.989 | 34.9887 | 34.99 | 34.9875 | 34.9897 | 34.9872 | 57.9518 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0477 | 2.8693 | 3.917
2025-01-15 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.29 | 1 |  | 57.44 | 0.5335 | 26.6736 | 26.6736 | 0 | 0 | 0 | 26.6736 | 30.7664 | 8.7904 | 0 | 34.9887 | 34.9884 | 34.9897 | 34.9872 | 34.9894 | 34.9869 | 57.9482 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0548 | 2.8693 | 3.9242
2025-01-15 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.41 | 1 |  | 57.61 | 0.5331 | 26.6544 | 26.6544 | 0 | 0 | 0 | 26.6544 | 30.9556 | 8.8445 | 0 | 34.9884 | 34.9881 | 34.9894 | 34.9869 | 34.9891 | 34.9866 | 57.9445 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0613 | 2.8693 | 3.9307
2025-01-15 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.52 | 1 |  | 57.78 | 0.5327 | 26.6368 | 26.6368 | 0 | 0 | 0 | 26.6368 | 31.1432 | 8.8981 | 0 | 34.9881 | 34.9877 | 34.9891 | 34.9866 | 34.9888 | 34.9863 | 57.9409 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0678 | 2.8693 | 3.9371
2025-01-15 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.63 | 1 |  | 57.95 | 0.5324 | 26.6192 | 26.6192 | 0 | 0 | 0 | 26.6192 | 31.3308 | 8.9517 | 0 | 34.9877 | 34.9874 | 34.9888 | 34.9863 | 34.9884 | 34.9859 | 57.9373 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0742 | 2.8693 | 3.9435
2025-01-15 05:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.74 | 1 |  | 58.11 | 0.532 | 26.6016 | 26.6016 | 0 | 0 | 0 | 26.6016 | 31.5084 | 9.0024 | 0 | 34.9874 | 34.9871 | 34.9884 | 34.9859 | 34.9881 | 34.9856 | 57.9337 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0803 | 2.8693 | 3.9496
2025-01-15 06:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.84 | 1 |  | 58.26 | 0.5317 | 26.5856 | 26.5856 | 0 | 0 | 0 | 26.5856 | 31.6744 | 9.0498 | 0 | 34.9871 | 34.9868 | 34.9881 | 34.9856 | 34.9878 | 34.9853 | 57.93 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.086 | 2.8693 | 3.9553
2025-01-15 07:00 | 1 | seasonal | Long-Term / Seasonal Storage | -8.94 | 1 |  | 58.41 | 0.5314 | 26.5696 | 26.5696 | 0 | 0 | 0 | 26.5696 | 31.8404 | 9.0973 | 0 | 34.9868 | 34.9865 | 34.9878 | 34.9853 | 34.9875 | 34.985 | 57.9264 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.0917 | 2.8693 | 3.961
2025-01-15 08:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.03 | 1 |  | 58.55 | 0.5311 | 26.5552 | 26.5552 | 0 | 0 | 0 | 26.5552 | 31.9948 | 9.1414 | 0 | 34.9865 | 34.9862 | 34.9875 | 34.985 | 34.9872 | 34.9847 | 57.9228 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.097 | 2.8693 | 3.9663
2025-01-15 09:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.12 | 1 |  | 58.68 | 0.5308 | 26.5408 | 26.5408 | 0 | 0 | 0 | 26.5408 | 32.1392 | 9.1826 | 0 | 34.9862 | 34.9859 | 34.9872 | 34.9847 | 34.9869 | 34.9844 | 57.9192 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1019 | 2.8693 | 3.9713
2025-01-15 10:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.2 | 1 |  | 58.81 | 0.5306 | 26.528 | 26.528 | 0 | 0 | 0 | 26.528 | 32.282 | 9.2234 | 0 | 34.9859 | 34.9856 | 34.9869 | 34.9844 | 34.9866 | 34.9841 | 57.9156 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1068 | 2.8693 | 3.9762
2025-01-15 11:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.29 | 1 |  | 58.93 | 0.5303 | 26.5136 | 26.5136 | 0 | 0 | 0 | 26.5136 | 32.4164 | 9.2618 | 0 | 34.9856 | 34.9852 | 34.9866 | 34.9841 | 34.9863 | 34.9838 | 57.9119 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1114 | 2.8693 | 3.9808
2025-01-15 12:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.36 | 1 |  | 59.04 | 0.53 | 26.5024 | 26.5024 | 0 | 0 | 0 | 26.5024 | 32.5376 | 9.2965 | 0 | 34.9852 | 34.9849 | 34.9863 | 34.9838 | 34.9859 | 34.9835 | 57.9083 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1156 | 2.8693 | 3.9849
2025-01-15 13:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.43 | 1 |  | 59.15 | 0.5298 | 26.4912 | 26.4912 | 0 | 0 | 0 | 26.4912 | 32.6588 | 9.3311 | 0 | 34.9849 | 34.9846 | 34.9859 | 34.9835 | 34.9856 | 34.9831 | 57.9047 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1197 | 2.8693 | 3.9891
2025-01-15 14:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.5 | 1 |  | 59.25 | 0.5296 | 26.48 | 26.48 | 0 | 0 | 0 | 26.48 | 32.77 | 9.3629 | 0 | 34.9846 | 34.9843 | 34.9856 | 34.9831 | 34.9853 | 34.9828 | 57.9011 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1235 | 2.8693 | 3.9929
2025-01-15 15:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.57 | 1 |  | 59.35 | 0.5294 | 26.4688 | 26.4688 | 0 | 0 | 0 | 26.4688 | 32.8812 | 9.3946 | 0 | 34.9843 | 34.984 | 34.9853 | 34.9828 | 34.985 | 34.9825 | 57.8974 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1274 | 2.8693 | 3.9967
2025-01-15 16:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.63 | 1 |  | 59.44 | 0.5292 | 26.4592 | 26.4592 | 0 | 0 | 0 | 26.4592 | 32.9808 | 9.4231 | 0 | 34.984 | 34.9837 | 34.985 | 34.9825 | 34.9847 | 34.9822 | 57.8938 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1308 | 2.8693 | 4.0001
2025-01-15 17:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.68 | 1 |  | 59.52 | 0.529 | 26.4512 | 26.4512 | 0 | 0 | 0 | 26.4512 | 33.0688 | 9.4482 | 0 | 34.9837 | 34.9834 | 34.9847 | 34.9822 | 34.9844 | 34.9819 | 57.8902 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1338 | 2.8693 | 4.0031
2025-01-15 18:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.73 | 1 |  | 59.6 | 0.5289 | 26.4432 | 26.4432 | 0 | 0 | 0 | 26.4432 | 33.1568 | 9.4734 | 0 | 34.9834 | 34.9831 | 34.9844 | 34.9819 | 34.9841 | 34.9816 | 57.8866 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1368 | 2.8693 | 4.0062
2025-01-15 19:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.78 | 1 |  | 59.67 | 0.5287 | 26.4352 | 26.4352 | 0 | 0 | 0 | 26.4352 | 33.2348 | 9.4957 | 0 | 34.9831 | 34.9828 | 34.9841 | 34.9816 | 34.9838 | 34.9813 | 57.883 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1395 | 2.8693 | 4.0088
2025-01-15 20:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.82 | 1 |  | 59.73 | 0.5286 | 26.4288 | 26.4288 | 0 | 0 | 0 | 26.4288 | 33.3012 | 9.5146 | 0 | 34.9828 | 34.9824 | 34.9838 | 34.9813 | 34.9835 | 34.981 | 57.8793 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1418 | 2.8693 | 4.0111
2025-01-15 21:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.86 | 1 |  | 59.79 | 0.5284 | 26.4224 | 26.4224 | 0 | 0 | 0 | 26.4224 | 33.3676 | 9.5336 | 0 | 34.9824 | 34.9821 | 34.9835 | 34.981 | 34.9831 | 34.9806 | 57.8757 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.144 | 2.8693 | 4.0134
2025-01-15 22:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.89 | 1 |  | 59.84 | 0.5284 | 26.4176 | 26.4176 | 0 | 0 | 0 | 26.4176 | 33.4224 | 9.5493 | 0 | 34.9821 | 34.9818 | 34.9831 | 34.9806 | 34.9828 | 34.9803 | 57.8721 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1459 | 2.8693 | 4.0153
2025-01-15 23:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.92 | 1 |  | 59.88 | 0.5283 | 26.4128 | 26.4128 | 0 | 0 | 0 | 26.4128 | 33.4672 | 9.5621 | 0 | 34.9818 | 34.9815 | 34.9828 | 34.9803 | 34.9825 | 34.98 | 57.8685 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1474 | 2.8693 | 4.0168
2025-01-16 | 1 | seasonal | Long-Term / Seasonal Storage | -9.94 | 1 |  | 59.92 | 0.5282 | 26.4096 | 26.4096 | 0 | 0 | 0 | 26.4096 | 33.5104 | 9.5744 | 0 | 34.9815 | 34.9812 | 34.9825 | 34.98 | 34.9822 | 34.9797 | 57.8649 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1489 | 2.8693 | 4.0183
2025-01-16 01:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.96 | 1 |  | 59.95 | 0.5281 | 26.4064 | 26.4064 | 0 | 0 | 0 | 26.4064 | 33.5436 | 9.5839 | 0 | 34.9812 | 34.9809 | 34.9822 | 34.9797 | 34.9819 | 34.9794 | 57.8612 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1501 | 2.8693 | 4.0194
2025-01-16 02:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.98 | 1 |  | 59.97 | 0.5281 | 26.4032 | 26.4032 | 0 | 0 | 0 | 26.4032 | 33.5668 | 9.5905 | 0 | 34.9809 | 34.9806 | 34.9819 | 34.9794 | 34.9816 | 34.9791 | 57.8576 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1509 | 2.8693 | 4.0202
2025-01-16 03:00 | 1 | seasonal | Long-Term / Seasonal Storage | -9.99 | 1 |  | 59.99 | 0.528 | 26.4016 | 26.4016 | 0 | 0 | 0 | 26.4016 | 33.5884 | 9.5967 | 0 | 34.9806 | 34.9803 | 34.9816 | 34.9791 | 34.9813 | 34.9788 | 57.854 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.1516 | 2.8693 | 4.021
2025-01-16 04:00 | 1 | seasonal | Long-Term / Seasonal Storage | -10 | 1 |  | 60 | 0.528 | 26.4 | 26.4 | 0 | 0 | 0 | 26.4 | 33.6 | 9.6 | 0 | 34.9803 | 34.9799 | 34.9813 | 34.9788 | 34.981 | 34.9785 | 57.8504 | 0 | 0 | 0 | 0 | 0.0036 | 0 | 1.152 | 2.8693 | 4.0213

## Optimized_Monthly
month | heating_load_kwh | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated
2025-01 | 13687.6 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 4042.8779 | 1201.5447 | 529.0192 | 522.0303 | 7.2218 | 144.1854 | 1047.3121 | 1191.4974

## Optimized_Annual
period | heating_load_kwh | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | auxiliary_energy_cost | capital_cost_allocated | total_cost_allocated | annualized_total_cost | solar_coverage_pct
annual | 13687.6 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 4042.8779 | 1201.5447 | 529.0192 | 522.0303 | 7.2218 | 144.1854 | 1047.3121 | 1191.4974 | 1191.4974 | 70.4632

## Optimize_Results
tank_type | tank_type_label | collector_area_m2 | tank_volume_m3 | tank_capacity_kwh | initial_tank_temp_c | tank_final_temp_c | heating_return_temp_c | seasonal_years_used | seasonal_converged | seasonal_max_years | collector_cost_per_m2 | collector_capital_cost | tank_capital_cost | annualized_capital_cost | annual_auxiliary_energy_cost | annualized_total_cost | solar_energy_collected_kwh | solar_direct_collector_to_load_kwh | solar_from_tank_direct_kwh | solar_from_tank_via_hp_kwh | solar_from_tank_via_hp_source_kwh | solar_source_energy_used_kwh | solar_energy_for_heating_kwh | auxiliary_heating_delivered_kwh | auxiliary_energy_input_kwh | auxiliary_energy_for_hp_boost_kwh | solar_energy_curtailed_kwh | tank_charge_kwh | tank_discharge_total_kwh | tank_loss_kwh | heating_load_kwh | solar_coverage_pct | auxiliary_fraction_pct
seasonal | Long-Term / Seasonal Storage | 50 | 10 | 580.8333 | 35 | 34.9799 | 35 | 1 | TRUE | 3 | 300 | 15000 | 5946.241 | 1047.3121 | 144.1854 | 1191.4974 | 28267.0522 | 9076.2551 | 405.9384 | 162.5286 | 116.0919 | 9598.2854 | 9644.7221 | 4042.8779 | 1201.5447 | 46.4367 | 18661.7779 | 529.0192 | 522.0303 | 7.2218 | 13687.6 | 70.4632 | 29.5368